## Jan'15
VTCAD January 2015 Operational Data
notes | Day of Jan 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
| 2 | 979.0995 | 55.3 | 115 | 2 | 606.6597 | 2925.7382 | 2 | 5.46 | 7.72 | 2 |  |  | 2 | [6 empty] | 13 | 0 | 36057 | 778
| 3 |  |  |  | 3 |  |  | 3 |  |  | 3 |  |  | 3
| 4 |  |  |  | 4 |  |  | 4 |  |  | 4 |  |  | 4
| 5 | 647.7509 | 55.5 | 60 | 5 | 546.1038 | 1771.1834 | 5 | 5.57 | 7.64 | 5 | 15.63 | 0.15 | 5 | 11125 | 600 | 9375 | 11700 | 9700 | 1500 | 16 | 93 | 38057 | 793
| 6 | 906.5567 | 54.3 | 180 | 6 | 606.6804 | 3241.2371 | 6 | 5.56 | 7.68 | 6 |  |  | 6 | [6 empty] | 9 | 4 | 38957 | 803
| 7 | 1546.6667 | 53.6 | 225 | 7 | 634.1818 | 3504.4848 | 7 | 5.9 | 7.74 | 7 |  |  | 7 | [6 empty] | 8 | 0 | 40557 | 813
| 8 | 519.2409 | 55.3 | 235 | 8 | 509.781 | 1231.8832 | 8 | 5.76 | 7.75 | 8 |  |  | 8 | [6 empty] | 3 | 86 | 41157 | 817
| 9 | 892.9933 | 57 | 225 | 9 | 523.8121 | 3162.2013 | 9 | 5.75 | 7.71 | 9 |  |  | 9 | [6 empty] | 8 | 1 | 42057 | 826
| 10 | 1000.1096 | 56.8 | 220 | 10 | 630.2466 | 3268.6027 | 10 | 5.76 | 7.68 | 10 |  |  | 10 | [6 empty] | 7 | 1 | 43057 | 836
| 11 | 892.2532 | 56.7 | 235 | 11 | 610.6329 | 3157.9747 | 11 | 5.72 | 7.67 | 11 |  |  | 11 | [6 empty] | 7 | 0 | 44057 | 846
| 12 | 816.2756 | 57.8 | 245 | 12 | 531.5833 | 10780.5086 | 12 | 6.1 | 7.76 | 12 |  |  | 12 | [6 empty] | 11 | 5 | 44757 | 852
| 13 | 648.5421 | 56.4 | 205 | 13 | 678.1109 | 3162.8747 | 13 | 5.79 | 7.8 | 13 |  |  | 13 | [6 empty] | 7 | 1 | 45757 | 862
| 14 | 856.2685 | 56.3 | 160 | 14 | 669.745 | 3031.7315 | 14 | 5.84 | 7.62 | 14 |  |  | 14 | [6 empty] | 7 | 2 | 46757 | 872
| 15 | 1048.2353 | 55.2 | 180 | 15 | 570.7059 | 3686.8235 | 15 | 5.76 | 7.51 | 15 |  |  | 15 | [6 empty] | 7 | 1 | 47657 | 881
| 16 | 868.7059 | 56.6 | 175 | 16 | 599.5294 | 3078.5882 | 16 | 5.62 | 7.66 | 16 |  |  | 16 | [6 empty] | 7 | 6 | 48557 | 890
| 17 | 938.0571 | 59.9 | 155 | 17 | 565.7143 | 3227.6571 | 17 | 5.58 | 7.65 | 17 |  |  | 17 | [6 empty] | 7 | 0 | 49457 | 899
| 18 | 920.6292 | 58.5 | 240 | 18 | 582.4719 | 2841.9775 | 18 | 5.41 | 7.59 | 18 |  |  | 18 | [6 empty] | 6 | 27 | 50657 | 909
| 19 | 541.44 |  |  | 19 | 407.04 | 1816.32 | 19 | 5.87 | 7.47 | 19 |  |  | 19 | [6 empty] | 4 | 0 | 51057 | 914
| 20 | 690.5722 | 55.4 | 50 | 20 | 418.8556 | 1673.4605 | 20 | 5.74 | 7.77 | 20 | 2.55 | 0.16 | 20 | 10125 | 2625 | 6700 | 9900 | 8150 | 1325 | 5 | 1 | 51757 | 919
| 21 |  | 54.5 | 120 | 21 | 410.0287 | 1559.6562 | 21 |  |  | 21 |  |  | 21 | [6 empty] | 10 | 3 | 52857 | 928
| 22 | 529.1691 | 56.9 | 120 | 22 | 449.6327 | 1857.3061 | 22 | 5.69 | 7.59 | 22 |  |  | 22 | [6 empty] | 8 | 5 | 53357 | 933
| 23 | 543.6735 | 56 | 100 | 23 | 501.8034 | 2150.7254 | 23 | 5.6 | 7.57 | 23 |  |  | 23 | [6 empty] | 9 | 0 | 54057 | 940
| 24 | 662.8881 | 57.2 | 95 | 24 | 523.0813 | 1950.8693 | 24 | 5.69 | 7.47 | 24 |  |  | 24 | [6 empty] | 8 | 0 | 54657 | 946
| 25 | 565.8233 | 59.2 | 150 | 25 | 576 | 2049.8221 | 25 | 5.73 | 7.43 | 25 |  |  | 25 | [6 empty] | 8 | 0 | 55257 | 952
| 26 | 598.548 | 57.2 | 155 | 26 | 590.026 | 2103.8961 | 26 |  |  | 26 |  |  | 26 | [6 empty] | 11 | 0 | 55857 | 959
| 27 | 612.4675 | 57.1 | 180 | 27 |  |  | 27 |  |  | 27 |  |  | 27
| 28 |  |  |  | 28 |  |  | 28 |  |  | 28 |  |  | 28
| 29 | 1478.4 | 57.7 | 205 | 29 | 1364.2667 | 5085.8667 | 29 | 6.17 | 7.67 | 29 |  |  | 29 | [6 empty] | 15 | 0 | 57257 | 973
| 30 | 719.5152 | 56.4 | 185 | 30 | 654.5455 | 2447.5152 | 30 |  | 7.63 | 30 |  |  | 30 | [6 empty] | 7 | 0 | 58057 | 980
| 31 | 761.6 | 55.2 | 150 | 31 | 680.2286 | 2748.3429 | 31 |  |  | 31 |  |  | 31 | [6 empty] | 9 | 0 | 58857 | 989
| average | 814.8262 | 56.4615 | 167.8846 |  | 593.9026 | 2981.4326 |  | 5.7305 | 7.6426 |  |  | 0.155 | average | 10625 |  | 8037.5 | 10800 | 8925 | 1412.5
| SD | 262.0081 | 1.4678 | 55.4287 |  | 176.0286 | 1799.7309 |  | 0.18028 | 0.10109 |  |  | 0.0070711 | SD | 707.1068 |  | 1891.5106 | 1272.7922 | 1096.0155 | 123.7437

## Feb'15
VTCAD February 2015 Operational Data
notes | Day of Feb 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 849.1429 | 55.7 | 155 | 1 | 561.1429 | 2818.2857 | 1 |  |  | 1 |  |  | 1 | [6 empty] | 7 | 0 | 59657 | 997
| 2 | 869.8182 | 58.4 | 130 | 2 | 577.9394 | 2736.4848 | 2 | 6.1 | 7.56 | 2 |  |  | 2 | [6 empty] | 16 | 0 | 60557 | 1005
| 3 | 784.9412 | 55.4 | 110 | 3 | 587.2941 | 2535.5294 | 3 | 6.19 | 7.64 | 3 |  |  | 3 | [6 empty] | 9 | 0 | 61357 | 1013
| 4 | 782.8131 | 58.1 | 125 | 4 | 560.6172 | 2486.8843 | 4 | 6.28 | 7.73 | 4 |  |  | 4 | [6 empty] | 8 | 4 | 62357 | 1021
| 5 | 625.8065 | 59.9 | 70 | 5 | 535.4839 | 2201.2903 | 5 | 6.16 | 7.71 | 5 |  |  | 5 | [6 empty] | 5 | 0 | 62857 | 1026
| 6 | 571.3808 | 57.2 | 100 | 6 | 580.4184 | 2013.3891 | 6 | 6.08 | 7.58 | 6 |  |  | 6 | [6 empty] | 8 | 0 | 63357 | 1032
| 7 | 726.8073 | 55.7 | 75 | 7 | 549.8182 | 2482.0364 | 7 | 6.11 | 7.66 | 7 |  |  | 7 | [6 empty] | 6 | 0 | 64057 | 1039
| 8 | 548 | 54.2 | 95 | 8 | 538 | 1930 | 8 | 6.11 | 7.63 | 8 |  |  | 8 | [6 empty] | 6 | 0 | 64657 | 1045
| 9 | 414.4807 | 55.8 | 105 | 9 | 582.8368 | 1414.362 | 9 | 6.23 | 7.69 | 9 |  |  | 9 | [6 empty] | 5 | 34 | 65157 | 1050
| 10 | 950.4441 | 54.9 | 170 | 10 | 605.3292 | 3060.827 | 10 | 6.27 | 7.73 | 10 |  |  | 10 | [6 empty] | 8 | 0 | 66057 | 1058
| 11 | 831.8397 | 54.8 | 180 | 11 | 593.7294 | 2945.9699 | 11 | 6.14 | 7.66 | 11 |  |  | 11 | [6 empty] | 6 | 0 | 66857 | 1066
| 12 | 1270.4023 | 53.9 | 220 | 12 | 595.1719 | 3497.2933 | 12 | 6.24 | 7.57 | 12 |  |  | 12 | [6 empty] | 9 | 4 | 68057 | 1076
| 13 | 1638.2466 | 49.3 | 220 | 13 | 742.6849 | 3568.4384 | 13 | 6.13 | 7.55 | 13 |  |  | 13 | [6 empty] | 11 | 1 | 69757 | 1086
| 14 | 1518.8911 | 49.3 | 340 | 14 | 703.3663 | 3136.6337 | 14 | 6.1 | 7.56 | 14 |  |  | 14 | [6 empty] | 7 | 6 | 71357 | 1096
| 15 | 189.3426 | 55.3 | 195 | 15 | 556.0692 | 413.564 | 15 | 6.2 | 7.71 | 15 |  |  | 15 | [6 empty] | 1 | 39 | 71557 | 1097
| 16 | 728 | 56.5 | 95 | 16 | 557 | 2695 | 16 |  |  | 16 |  |  | 16 | [6 empty] | 6 | 5 | 72257 | 1105
| 17 | 181.5652 | 56.6 | 245 | 17 | 690.7826 | 655.3043 | 17 | 5.81 | 7.78 | 17 |  |  | 17 | [6 empty] | 2 | 168 | 72457 | 1107
| 18 | 1373.7084 | 52.9 | 260 | 18 | 694.2199 | 3586.1893 | 18 | 6.05 | 7.54 | 18 |  |  | 18 | [6 empty] | 7 | 0 | 73957 | 1118
| 19 | 1397.1109 | 52.2 | 245 | 19 | 595.0856 | 3048.3395 | 19 | 5.92 | 7.58 | 19 |  |  | 19 | [6 empty] | 8 | 2 | 75257 | 1126
| 20 | 1359.4066 | 46.5 | 290 | 20 | 635.0371 | 2862.5219 | 20 |  |  | 20 |  |  | 20 | [6 empty] | 7 | 6 | 76757 | 1134
| 21 | 1403.2156 | 52 | 270 | 21 | 781.127 | 2994.6807 | 21 | 5.73 | 7.54 | 21 |  |  | 21 | [6 empty] | 9 | 0 | 78057 | 1143
| 22 | 1577.1429 | 53.4 | 280 | 22 | 643.9752 | 3449.441 | 22 | 5.6 | 7.53 | 22 |  |  | 22 | [6 empty] | 9 | 1 | 79657 | 1153
| 23 | 1303.1852 | 54.3 | 270 | 23 | 569.8975 | 2991.2235 | 23 | 5.59 | 7.54 | 23 |  |  | 23 | [6 empty] | 8 | 0 | 80957 | 1161
| 24 |  | 50.4 | 345 | 24 |  |  | 24 |  |  | 24 |  |  | 24
| 25 | 2621.7674 | 53.5 | 340 | 25 | 967.4419 | 5826.9767 | 25 | 5.2 | 7.57 | 25 |  |  | 25 | [6 empty] | 18 | 14 | 84557 | 1184
| 26 | 615.2224 | 54.6 | 260 | 26 | 707.743 | 1553.8715 | 26 |  |  | 26 |  |  | 26 | [6 empty] | 3 | 220 | 85357 | 1189
| 27 | 1394.3478 | 55.2 | 210 | 27 | 536.087 | 4335.6522 | 27 | 5.26 | 7.59 | 27 |  | 0.21 | 27 |  |  |  | 9000 | 7425 | 1550 | 7 | 5 | 86457 | 1199
| 28 | 1248 | 54.7 | 185 | 28 | 597.4468 | 4388.4255 | 28 |  |  | 28 |  |  | 28 | [6 empty] | 9 | 0 | 87657 | 1211
| average | 1028.7048 | 54.3107 | 199.4643 | average | 623.9165 | 2801.0598 |  | 5.9773 | 7.6205 |  |  | 0.21 | average | #DIV/0! |  | #DIV/0! | 9000 | 7425 | 1550
| SD | 527.9551 | 2.922 | 84.4299 | SD | 95.899 | 1114.4055 |  | 0.31418 | 0.076562 |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Mar'15
VTCAD March 2015 Operational Data
notes | Day of Mar 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 1302.9517 | 55.1 | 155 | 1 | 573.0207 | 4842.3724 | 1 | 5.19 | 7.58 | 1 |  |  | 1 | [6 empty] | 9 | 0 | 88957 | 1225
| 2 | 1206.2466 | 55.6 | 180 | 2 | 563.1781 | 4530.0822 | 2 | 5.16 | 7.61 | 2 |  |  | 2 | [6 empty] | 8 | 0 | 90257 | 1238
| 3 | 1415.1111 | 55.4 | 380 | 3 | 818.6667 | 4743.1111 | 3 |  |  | 3 |  |  | 3 | [6 empty] | 9 | 0 | 91857 | 1253
| 4 | 2120.5161 | 53.7 | 265 | 4 | 593.4194 | 4587.0968 | 4 | 5.3 | 7.54 | 4 |  |  | 4 | [6 empty] | 7 | 0 | 93657 | 1265
| 5 | 2114.6218 | 52.5 | 300 | 5 | 687.7311 | 4724.3697 | 5 | 5.41 | 7.64 | 5 |  |  | 5 | [6 empty] | 8 | 0 | 95757 | 1278
| 6 | 2122.1584 | 51.7 | 65 | 6 | 618.5844 | 4646.9516 | 6 | 5.61 | 7.62 | 6 |  |  | 6 | [6 empty] | 8 | 0 | 97957 | 1291
| 7 | 1887.4788 | 54.5 | 10 | 7 | 710.1498 | 4486.9837 | 7 | 5.59 | 7.57 | 7 |  |  | 7 | [6 empty] | 9 | 0 | 99957 | 1305
| 8 | 1972.1041 | 54.8 | 25 | 8 | 549.2342 | 4662.6022 | 8 | 5.61 | 7.56 | 8 |  |  | 8 | [6 empty] | 7 | 0 | 101857 | 1317
| 9 | 2269.0909 | 54.8 | 45 | 9 | 659.3939 | 5196.6061 | 9 |  |  | 9 |  |  | 9 | [6 empty] | 8 | 0 | 104157 | 1332
| 10 | 2100.3956 | 54.7 | 290 | 10 | 734.2418 | 4990.9451 | 10 | 5.57 | 7.68 | 10 |  |  | 10 | [6 empty] | 7 | 0 | 106257 | 1345
| 11 | 1859.7898 | 50.6 | 890 | 11 | 628.6755 | 4082.8591 | 11 | 5.42 | 7.67 | 11 |  |  | 11 | [6 empty] | 7 | 0 | 108057 | 1357
| 12 | 1910.8475 | 53.7 | 415 | 12 | 596.9492 | 4289.4915 | 12 | 5.56 | 7.68 | 12 |  |  | 12 | [6 empty] | 8 | 0 | 109957 | 1369
| 13 | 894.6304 | 54 | 275 | 13 | 719.0661 | 2477.5097 | 13 | 5.57 | 7.6 | 13 |  |  | 13 | [6 empty] | 5 | 0 | 110579 | 1377
| 14 | 2394.596 | 52.8 | 265 | 14 | 641.8013 | 5897.3245 | 14 | 5.69 | 7.58 | 14 |  |  | 14 | [6 empty] | 7 | 0 | 113457 | 1394
| 15 | 2514.4207 | 54.3 | 180 | 15 | 574.9373 | 5463.4982 | 15 | 5.57 | 7.46 | 15 |  |  | 15 | [6 empty] | 7 | 0 | 115857 | 1408
| 16 | 2876.0276 | 54.6 | 515 | 16 | 649.4897 | 6863.3379 | 16 |  |  | 16 |  |  | 16 | [6 empty] | 5 | 0 | 118857 | 1428
| 17 | 3196.2947 | 48.6 | 1555 | 17 | 722.5263 | 6812.9684 | 17 |  |  | 17 |  |  | 17 | [6 empty] | 6 | 0 | 122057 | 1446
| 18 | 2211 | 56.1 | 270 | 18 | 734 | 6043 | 18 | 5.47 | 7.37 | 18 |  |  | 18 | [6 empty] | 8 | 0 | 124257 | 1463
| 19 | 1826.0426 | 57.8 | 180 | 19 | 581.1064 | 6786.383 | 19 | 5.48 | 7.54 | 19 |  |  | 19 | [6 empty] | 6 | 0 | 126057 | 1482
| 20 | 2317.6331 | 58 | 85 | 20 | 700.5917 | 7876.9231 | 20 | 5.51 | 7.52 | 20 |  |  | 20 | [6 empty] | 5 | 0 | 124557 | 1504
| 21 | 2169.6406 | 58.4 | 205 | 21 | 724.5666 | 7886.0042 | 21 |  |  | 21 |  |  | 21 | [6 empty] | 5 | 0 | 130757 | 1523
| 22 | 1981.8129 | 58 | 265 | 22 | 600.8633 | 7453.8129 | 22 | 5.15 | 7.27 | 22 |  |  | 22 | [6 empty] | 4 | 0 | 132657 | 1545
| 23 | 1807.4483 | 57.5 | 260 | 23 | 627.6414 | 6893.131 | 23 | 5.17 | 7.47 | 23 |  |  | 23 | [6 empty] | 2 | 0 | 134557 | 1564
| 24 | 2212.6829 | 57.4 | 275 | 24 | 662.2997 | 8554.7038 | 24 | 5.08 | 7.45 | 24 |  |  | 24 | [6 empty] | 1 | 0 | 136757 | 1587
| 25 | 2322.3624 | 56.9 | 130 | 25 | 676.5101 | 9027.5436 | 25 | 5.03 | 7.5 | 25 |  |  | 25 | [6 empty] | 0 | 0 | 139257 | 1613
| 26 | 2133.5256 | 58.7 | 83 | 26 | 588.6662 | 7995.2704 | 26 | 5.05 | 7.52 | 26 |  |  | 26 | [6 empty] | 1 | 0 | 141357 | 1633
| 27 | 2434.453 | 57 | 385 | 27 | 632.1951 | 6522.6481 | 27 | 5.06 | 7.43 | 27 |  |  | 27 | [6 empty] | 1 | 0 | 143757 | 1651
| 28 | 2814.3646 | 55.3 | 110 | 28 | 646.4088 | 8059.2265 | 28 | 4.89 | 7.51 | 28 |  |  | 28 | [6 empty] | 1 | 0 | 146657 | 1674
| 29 | 2614.7629 | 55.8 | 120 | 29 | 577.9794 | 8101.6082 | 29 | 4.91 | 7.74 | 29 |  |  | 29 | [6 empty] | 1 | 0 | 149357 | 1698
| 30 | 2212.5653 | 56.1 | 195 | 30 | 566.1621 | 7303.2016 | 30 | 4.92 | 7.58 | 30 |  |  | 30 | [6 empty] | 3 | 0 | 151657 | 1720
| 31 | 2095.5066 | 58.1 | 165 | 31 | 685.1101 | 7277.1806 | 31 | 4.92 | 7.74 | 31 |  |  | 31 | [6 empty] | 2 | 0 | 153657 | 1739
| average | 2106.8091 | 55.1467 | 279.1 | average | 645.3352 | 6099.3144 |  | 5.3188 | 7.5476 |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| SD | 476.243 | 2.3598 | 296.2748 | SD | 66.1313 | 1625.1074 |  | 0.2594 | 0.10453 |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Apr'15
VTCAD April 2015 Operational Data
notes | Day of Apr 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 2778.5635 | 58.6 | 120 | 1 | 708.0663 | 8442.0994 | 1 | 4.96 | 7.5 | 1 |  |  | 1 | [6 empty] | 0 | 0 | 156457 | 1763
| 2 | 2929.7561 | 57 | 130 | 2 | 743.4146 | 8403.9024 | 2 |  |  | 2 |  |  | 2 | [6 empty] | 0 | 0 | 159557 | 1788
| 3 |  |  |  | 3 |  |  | 3 |  |  | 3 |  |  | 3
| 4 | 2223.5519 | 57.9 | 130 | 4 | 597.235 | 7098.9295 | 4 | 4.82 | 7.91 | 4 |  |  | 4 | [6 empty] | 3 | 0 | 163957 | 1828
| 5 |  |  |  | 5 |  |  | 5 |  |  | 5 |  |  | 5
| 6 | 2595.8217 | 57.1 | 85 | 6 | 607.5536 | 7695.3522 | 6 | 4.84 | 7.4 | 6 |  |  | 6 | [6 empty] | 6 | 0 | 169257 | 1873
| 7 | 2589.1221 | 42.8 | 130 | 7 | 629.0364 | 7695.4176 | 7 | 4.85 | 7.69 | 7 |  | 0.48333 | 7 | 2600 |  | 1500 | 5891.6667 | 3775 | 1825 | 3 | 0 | 171957 | 1895
| 8 | 2544 | 55.8 | 155 | 8 | 659 | 7582 | 8 | 4.8 | 7.35 | 8 |  |  | 8 | [6 empty] | 3 | 0 | 174457 | 1916
| 9 | 2410.7317 | 55.4 | 160 | 9 | 709.2683 | 7545.3659 | 9 | 4.82 | 7.51 | 9 |  |  | 9 | [6 empty] | 4 | 0 | 176957 | 1938
| 10 | 2105.4857 | 54.8 | 180 | 10 | 622.2857 | 6993.2571 | 10 | 4.89 | 7.46 | 10 |  | 0.52333 | 10 | 2383.3333 |  | 1191.6667 | 5650 | 3525 | 1850 | 5 | 0 | 179057 | 1958
| 11 | 1607.6647 | 54.8 | 145 | 11 | 675.4491 | 5937.2455 | 11 |  |  | 11 |  |  | 11 | [6 empty] | 6 | 8 | 180575 | 1976
| 12 | 1690.677 | 54.7 | 160 | 12 | 640.619 | 5957.7563 | 12 |  |  | 12 |  |  | 12 | [6 empty] | 9 | 0 | 182157 | 1995
| 13 | 1575.4625 | 54.1 | 170 | 13 | 612.4269 | 5621.1225 | 13 | 4.88 | 7.33 | 13 |  | 0.50667 | 13 | 2541.6667 |  | 1366.6667 | 5558.3333 | 3483.3333 | 1766.6667 | 9 | 0 | 183957 | 2010
| 14 | 1532.3959 | 54.4 | 170 | 14 | 622.198 | 5582.0887 | 14 | 4.96 | 7.39 | 14 |  |  | 14 | [6 empty] | 6 | 0 | 185557 | 2027
| 15 | 1499.234 | 48.9 | 180 | 15 | 695.4894 | 5544.5106 | 15 | 5 | 7.45 | 15 |  |  | 15 | [6 empty] | 6 | 0 | 187057 | 2043
| 16 | 1446.2031 | 48.3 | 185 | 16 | 731.0769 | 5150.3262 | 16 | 5.02 | 7.35 | 16 |  |  | 16 | [6 empty] | 8 | 0 | 188657 | 2060
| 17 | 1391.8088 | 54.7 | 170 | 17 | 553.0518 | 5087.6175 | 17 | 5.04 | 7.34 | 17 |  | 0.54333 | 17 | 2833.3333 |  | 1758.3333 | 5516.6667 | 3383.3333 | 1841.6667 | 7 | 0 | 189957 | 2073
| 18 | 1443.9184 | 48.5 | 180 | 18 | 709.2245 | 4810.7755 | 18 | 5.11 | 7.36 | 18 |  |  | 18 | [6 empty] | 7 | 0 | 191475 | 2087
| 19 | 1392 | 48.4 | 155 | 19 | 613 | 4825 | 19 | 5.14 | 7.36 | 19 |  |  | 19 | [6 empty] | 8 | 0 | 192857 | 2102
| 20 | 1205.3706 |  |  | 20 | 664.6154 | 4391.4965 | 20 | 5.18 | 7.39 | 20 |  |  | 20 | [6 empty] | 8 | 0 | 194057 | 2115
| 21 | 1262.3833 | 47.2 | 155 | 21 | 598.0767 | 4033.0035 | 21 | 5.08 | 7.54 | 21 |  | 0.62667 | 21 | 2783.3333 |  | 1716.6667 | 6541.6667 | 3750 | 2358.3333 | 8 | 2 | 195357 | 2127
| 22 | 1680.8191 | 46.5 | 95 | 22 | 580.9147 | 3681.0922 | 22 | 5.15 | 7.5 | 22 |  |  | 22 | [6 empty] | 9 | 1 | 197057 | 2138
| 23 | 1738.1408 | 47.4 | 140 | 23 | 733.1831 | 3991.4366 | 23 | 5.08 | 7.43 | 23 |  |  | 23 | [6 empty] | 9 | 0 | 198557 | 2150
| 24 | 1438.9965 | 51.1 | 130 | 24 | 710.4669 | 3893.5192 | 24 | 5.03 | 7.35 | 24 |  | 0.52667 | 24 | 2408.3333 |  | 1441.6667 | 5550 | 3433.3333 | 1808.3333 | 8 | 4 | 200257 | 2162
| 25 | 1314.3093 | 46.9 | 75 | 25 | 711.5876 | 4049.8144 | 25 | 5.02 | 7.37 | 25 |  |  | 25 | [6 empty] | 9 | 4 | 201557 | 2174
| 26 | 1300.9655 | 49 | 50 | 26 | 649.4897 | 4067.7517 | 26 | 5.04 | 7.3 | 26 |  |  | 26 | [6 empty] | 9 | 6 | 202957 | 2186
| 27 | 1307.6211 | 48.5 | 110 | 27 | 588.1263 | 3624.7579 | 27 | 5.18 | 7.32 | 27 |  |  | 27 | [6 empty] | 8 | 1 | 204257 | 2197
AD vertical mixing pump 6 removed & used to replace hydrolyzer to AD pump that was sent out for service of a bent shaft. | 28 | 1353.0947 | 49 | 100 | 28 | 731.6211 | 3889.5158 | 28 | 5.22 | 7.23 | 28 |  |  | 28 | [6 empty] | 9 | 0 | 205557 | 2209
| 29 | 1691.5068 | 48.8 | 120 | 29 | 725.9178 | 4395.9452 | 29 | 5.18 | 7.19 | 29 |  |  | 29 | [6 empty] | 8 | 0 | 207357 | 2222
| 30 | 1557.2211 | 48.1 | 120 | 30 | 600.2526 | 4244.2105 | 30 | 5.08 | 7.22 | 30 |  |  | 30 | [6 empty] | 9 | 0 | 208857 | 2235
| average | 1771.6724 | 51.4333 | 137.037 | average | 657.9517 | 5508.4039 |  | 5.0148 | 7.4096 |  |  | 0.535 | average | 2591.6667 |  | 1495.8333 | 5784.7222 | 3558.3333 | 1908.3333
| SD | 520.0434 | 4.2844 | 35.2262 | SD | 56.5467 | 1566.8337 |  | 0.12926 | 0.15037 |  |  | 0.049295 | SD | 186.9343 |  | 214.3951 | 395.1588 | 165.328 | 222.4235

## May'15
VTCAD May 2015 Operational Data
notes: AD vertical mixing pump 6 out all month. | Day of May 2015 | biogas consumed (m3) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh) | electricity produced (kWh) | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
AD vertical mixing pump out all month. Worked on flare: raised position of thermocouple. | 1 | 1691.5717 | 60.3 | 222 | 1 | 694.3018 | 4035.9674 | 5.02 | 7.22 | 1 |  | 0.41667 | 1 | 1918.3333 |  | 1073.6667 | 6266.6667 | 4220 | 1742.6667 | 9 | 0 | 210757 | 2248
Conveyer 2 breaker tripped. | 2 | 1939.0202 |  | 174 | 2 | 641.1527 | 4885.4179 | 5.06 | 7.22 | 2 |  |  | 2 | [6 empty] | 9 | 0 | 212657 | 2262
Conveyer 2 breaker tripped. | 3 | 1746.7826 |  | 266 | 3 | 590.6087 | 5017.0435 | 5.04 | 7.22 | 3 |  |  | 3 | [6 empty] | 8 | 0 | 214357 | 2275
| 4 |  |  |  | 4 |  |  |  |  | 4 |  |  | 4
| 5 |  |  |  | 5 |  |  |  |  | 5 |  |  | 5
| 6 | 1624.761 | 62.3 | 194 | 6 | 646.4965 | 5000.9095 | 5.1 | 7.23 | 6 |  |  | 6 | [6 empty] | 26 | 2 | 219257 | 2318
| 7 | 1614.0881 | 61.2 | 364 | 7 | 672.2013 | 5689.5597 | 5.03 | 7.18 | 7 |  |  | 7 | [6 empty] | 8 | 0 | 220957 | 2334
Increased glycerol:crumb to 800 gallons/day. Increased flare on setting to 90%. Genset on setting is 80%. Calibrated gas analyzer. | 8 | 1594.912 | 61.4 | 289 | 8 | 623.5453 | 5422.8958 | 5.02 | 7.24 | 8 |  | 0.48 | 8 | 2450 |  | 1633.3333 | 6083.3333 | 3875 | 1866.6667 | 9 | 1 | 222557 | 2350
| 9 |  |  |  | 9 |  |  |  |  | 9 |  |  | 9
Changed FeCl3 tote. | 10 | 1641.9299 | 60.7 | 369 | 10 | 581.2982 | 5229.6841 |  |  | 10 |  |  | 10 | [6 empty] | 17 | 0 | 225857 | 2379
| 11 | 2137.0637 | 60.5 | 350 | 11 | 561.4404 | 4945.2632 |  |  | 11 |  |  | 11 | [6 empty] | 9 | 0 | 228157 | 2394
Genset tripped off x 2; flare worked first time but was turned off second time? | 12 | 1882.5974 | 60.3 | 275 | 12 | 554.8052 | 4431.1688 | 5.25 | 7.17 | 12 |  |  | 12 | [6 empty] | 9 | 6 | 229957 | 2406
| 13 | 1351.6138 | 60 | 262 | 13 | 628.6345 | 3031.9448 | 5.25 | 7.23 | 13 |  |  | 13 | [6 empty] | 6 | 1 | 231257 | 2415
| 14 | 1708.4082 | 60.5 | 342 | 14 | 491.7551 | 4415.0204 |  |  | 14 |  |  | 14 | [6 empty] | 9 | 0 | 233057 | 2428
| 15 | 1783.7288 | 60.3 | 330 | 15 | 627.4576 | 4448.1356 | 5.14 | 7.32 | 15 |  | 0.6075 | 15 | 2825 |  | 2025 | 6168.75 | 3637.5 | 2200 | 8 | 0 | 234857 | 2440
Ammonia in prep pit; connected to moldy silage fed yesterday? | 16 | 1964.1926 | 60 | 323 | 16 | 509.915 | 4303.6827 | 5.19 | 7.15 | 16 |  |  | 16 | [6 empty] | 9 | 0 | 236757 | 2452
| 17 |  | 59.9 | 358 | 17 |  |  |  |  | 17 |  |  | 17
Flushed ~100 gallons from bottom of AD tank. | 18 | 4249.61 | 59.6 | 432 | 18 | 1207.8627 | 9188.8924 | 5.35 | 7.13 | 18 |  |  | 18 | [6 empty] | 27 | 0 | 240557 | 2475
| 19 | 1870.9202 | 59.5 | 295 | 19 | 596.8098 | 4032.3926 | 5.13 | 7.13 | 19 |  |  | 19 | [6 empty] | 9 | 0 | 242557 | 2987
| 20 |  |  |  | 20 |  |  |  |  | 20 |  |  | 20
Flushed ~1000 gallons from bottom of AD tank. | 21 | 1945.1309 | 60.2 | 320 | 21 | 549.3613 | 4200.8796 | 5.04 | 7.21 | 21 |  | 0.63667 | 21 | 2491.6667 |  | 1725 | 6066.3333 | 3458.3333 | 2200 | 18 | 1 | 246457 | 2511
Pump 11 running fault | 22 | 2052.3789 | 61.1 | 480 | 22 | 496.1684 | 4417.0105 |  |  | 22 |  |  | 22 | [6 empty] | 10 | 0 | 248457 | 2524
Pump 12 running fault | 23 | 1579 | 62.3 | 329 | 23 | 532 | 4566 | 5.19 | 7.13 | 23 |  |  | 23 | [6 empty] | 9 | 0 | 250057 | 2537
Genset tripped off; flare working. Conveyer 2 breaker tripped. | 24 | 1348.3183 | 63.2 | 413 | 24 | 577.9931 | 5140.1522 |  |  | 24 |  |  | 24 | [6 empty] | 8 | 6 | 251457 | 2552
| 25 | 1535.3379 | 63.2 | 333 | 25 | 504.4966 | 6031.1172 | 5.11 | 7.13 | 25 |  |  | 25 | [6 empty] | 7 | 0 | 253057 | 2569
| 26 | 1536 | 62 | 367 | 26 | 530 | 5710 | 5.43 | 7.05 | 26 |  |  | 26 | [6 empty] | 8 | 0 | 254557 | 2585
Lightning storm shut system down; Dan reset. Calibrated gas analyzer. | 27 | 2178.436 | 61.8 | 400 | 27 | 589.9516 | 5443.1003 | 5.19 | 7.03 | 27 |  |  | 27 | [6 empty] | 9 | 0 | 256757 | 2600
Ammonia in prep pit | 28 | 1749.0732 | 60.7 | 263 | 28 | 437.5192 | 4815.7213 | 5.13 | 6.99 | 28 |  |  | 28 | [6 empty] | 7 | 11 | 258557 | 2614
Genset switch closing fault | 29 | 1784.2827 | 61.9 | 196 | 29 | 540.8732 | 5414.7193 | 5.35 | 7.12 | 29 |  | 0.83667 | 29 | 2683.3333 |  | 1958.3333 | 5650 | 2850 | 2391.6667 | 9 | 0 | 260357 | 2629
Genset tripped off; flare working | 30 | 588.4955 |  |  | 30 | 544.1568 | 1960.9797 |  |  | 30 |  |  | 30 | [6 empty] | 3 | 4 | 260957 | 2635
| 31 | 1756.4265 |  |  | 31 | 531.1816 | 5313.8905 |  |  | 31 |  |  | 31 | [6 empty] | 9 | 0 | 262657 | 2649
| average | 1802.08 | 60.9957 | 317.84 | average | 594.6918 | 4888.1365 | 5.1589 | 7.1632 |  |  | 0.5955 | average | 2473.6667 |  | 1683.0667 | 6047.0167 | 3608.1667 | 2080.2
| SD | 587.2612 | 1.0856 | 75.8621 | SD | 138.9949 | 1226.8537 | 0.12183 | 0.081176 |  |  | 0.16227 | SD | 345.2081 |  | 376.9252 | 235.7856 | 510.8002 | 267.0397

## Jun'15
VTCAD June 2015 Operational Data | [23 empty] | VTCAD June 2015 Operational Data
Day of June 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs) | notes | Day of June 2015 | Genset tripped off | Flare started manually | Conveyer 2 breaker tripped | AD vertical mixing pump out | Calibrated gas analyzer | Vent fan filters installed | 2G service; genset oil changed | Separator plugged w/ woodchips | AD plug flushed
1 | 1237.3333 | 61.4 | 272 | 1 | 505.2121 | 4757.3333 | 1 | 5.35 | 7.02 | 1 |  |  | 1 | [6 empty] | 9 | 0 | 263957 | 2663 | Manually emptied flare water trap. Hicks started work on grinder conveyer belt. | 1 |  |  |  | 4
2 | 801.6495 | 61.1 | 300 | 2 | 578.9691 | 2987.8763 | 2 |  |  | 2 |  |  | 2 | [6 empty] | 7 | 5 | 264757 | 2672 | Genset tripped off; flare manually started. | 2 | 1 | 2 |  | 4
3 |  |  |  | 3 |  |  | 3 |  |  | 3 |  |  | 3 | [10 empty] | Genset tripped off: heard it start and quickly shut down. Manully restarted. Sent genset breaker images to Greg Martin at 2G; he will call back with recommendations. | 3 | 1 |  |  | 4
4 | 549 | 61.3 | 313 | 4 | 247 | 2111 | 4 | 5.15 | 7.02 | 4 |  | 0.85667 | 4 | 2837.5 |  | 1914.3333 | 5725 | 2825 | 2416.6667 | 9 | 1 | 267257 | 2698 | Conveyer belt #2 tripped off | 4 |  |  | 3 | 4
5 | 694.4959 | 60.6 | 334 | 5 | 540.4905 | 2671.0627 | 5 |  |  | 5 |  |  | 5 | [6 empty] | 5 | 4 | 267257 | 2706 | Genset tripped off & flare failed to start. Tested flare autostart successfully. Travis increased amperage settings on genset breakers in consultation with 2G's Mitch Lankford. Genset tripped off again. 2G will discuss and reply. Hicks installed conver belt up to grinder. | 5 | 1 | 2 |  | 4
6 | 1143.3217 | 59.7 | 354 | 6 | 559.047 | 4193.8612 | 6 |  |  | 6 |  |  | 6 | [6 empty] | 9 | 0 | 269151 | 2718 | Genset tripped off and restarted. | 6 | 1 |  |  | 4
7 | 820.898 |  |  | 7 | 538.7755 | 3166.0408 | 7 |  |  | 7 |  |  | 7 | [6 empty] | 7 | 1 | 269957 | 2727 | Genset tripped off and restarted. | 7 | 1 |  |  | 4
8 | 718.4106 |  |  | 8 | 452.4503 | 2670.1987 | 8 | 5.34 | 7.09 | 8 |  | 0.85 | 8 | [6 empty] | 6 | 4 | 270657 | 2734 | AD vertical mixing pump replaced. Genset tripped off twice & was manually restarted. | 8 | 1
9 | 1174.3396 | 57.5 | 242 | 9 | 608.805 | 3351.9497 | 9 | 5.08 | 7.06 | 9 |  |  | 9 | [6 empty] | 7 | 0 | 271857 | 2744 | Tested flare: worked on 2nd try. Calibrated gas analyzer. Partial install of vent fan filters. Auto tested flare again, successfully. | 9 |  |  |  |  | 5 | 6
10 | 1001.6963 | 60.3 | 521 | 10 | 544.6785 | 2377.6744 | 10 |  |  | 10 |  |  | 10 | [6 empty] | 6 | 2 | 272857 | 2751 | Flare started manually because biogas at 100%. Genset tripped off and manually restarted. Adjusted switch on conveyer belt 2. | 10 | 1 | 2
11 | 1474.0541 | 60.8 | 435 | 11 | 577.9459 | 3541.6216 | 11 | 4.97 | 7.04 | 11 |  |  | 11 | [6 empty] | 9 | 1 | 274357 | 2762 | Sniff test guy (?). 2G Valk. Dan worked on conveyer #2. | 11 | [6 empty] | 7
12 | 1022.2222 | 60.5 | 342 | 12 | 574.8148 | 2956.0494 | 12 | 4.88 | 7.11 | 12 |  | 0.79667 | 12 | 1766.6667 |  | 991.6667 | 5179.1667 | 2650 | 2108.3333 | 11 | 7 | 275457 | 2771 |  | 12
13 | 1385.6 | 59.8 | 487 | 13 | 535.4667 | 3224.5333 | 13 |  |  | 13 |  |  | 13 | [6 empty] | 7 | 1 | 276757 | 2780 | AD overflow box plugged with woodchips. Separator plugged. | 13 | [7 empty] | 8
14 | 600.4135 | 59.5 | 539 | 14 | 538.8835 | 1848.8766 | 14 |  |  | 14 |  |  | 14 | [6 empty] | 5 | 13 | 277357 | 2785 |  | 14
15 | 923.5443 | 58.9 | 275 | 15 | 618.8788 | 2926.8716 | 15 |  |  | 15 |  |  | 15 | [6 empty] | 8 | 0 | 278457 | 2795 | Separator pipe plugged twice; used balloon to remove blockage. Adjusted weights on separator to lower resistance. Abundant woodchips observed & scooped out of AD overflow box. Genset oil changed; oil pH 5 - 6. Flare autostart tested & failed. Started manually. Retest of autostart worked. | 15 |  | 2 | [5 empty] | 8
16 | 996.8354 | 58.4 | 306 | 16 | 502.4051 | 2587.2152 | 16 | 5.16 | 7.09 | 16 |  |  | 16 | [6 empty] | 7 | 0 | 279357 | 2802 | Separator plugged. Pulled chips from bottom of AD. | 16 | [7 empty] | 8 | 9
17 | 1064.5272 | 58 | 399 | 17 | 617.8797 | 2586.0172 | 17 | 5.1 | 7.1 | 17 |  |  | 17 | [6 empty] | 7 | 1 | 280357 | 2809 |  | 17
18 | 994.2628 | 58.3 | 465 | 18 | 652.2748 | 2872.3149 | 18 | 5.2 | 7.16 | 18 |  | 0.73333 | 18 | 2225 |  | 1475 | 5150 | 2733.3333 | 2000 | 8 | 0 | 281457 | 2818 | Alliance mechanical working on carbon filters for odor control. | 18 | [5 empty] | 6
19 | 1238.2418 | 57.7 | 368 | 19 | 568.6813 | 2876.044 | 19 | 5.2 | 7.14 | 19 |  |  | 19 | [6 empty] | 8 | 0 | 282757 | 2827 | Conveyer belt 2 breaker tripped x2 | 19 |  |  | 3
20 | 935.4894 | 57.8 | 297 | 20 | 555.5745 | 2741.1064 | 20 | 5.16 | 7.13 | 20 |  |  | 20 | [6 empty] | 7 | 0 | 283657 | 2835 | Conveyer belt 2 breaker tripped x1 | 20 |  |  | 3
21 | 1123.4851 | 57.2 | 378 | 21 | 410.6139 | 2776.396 | 21 | 5.15 | 7.11 | 21 |  |  | 21 | [6 empty] | 8 | 0 | 284857 | 2844 | Conveyer belt 2 breaker tripped x1 | 21 |  |  | 3
22 | 1153.0435 | 56.6 | 210 | 22 | 367.3043 | 2529.3913 | 22 | 5.25 | 7.16 | 22 |  |  | 22 | [6 empty] | 7 | 0 | 285957 | 2851 | Conveyer belt 2 breaker tripped x1; tightened chain on conveyer 1 | 22 |  |  | 3
23 | 1134.5143 | 56 | 298 | 23 | 380.5714 | 2482.9714 | 23 | 5.42 | 7.12 | 23 |  |  | 23 | [6 empty] | 7 | 0 | 287057 | 2858 | Night check normal; no odors | 23
24 | 1161 | 55.5 | 214 | 24 | 374 | 2514 | 24 | 5.29 | 7.12 | 24 |  |  | 24 | [6 empty] | 7 | 0 | 288257 | 2866 |  | 24
25 | 1092 | 55.9 | 130 | 25 | 384 | 2534 | 25 | 5.27 | 7.18 | 25 |  |  | 25 | [6 empty] | 8 | 0 | 289357 | 2873 | Calibrated gas analyzer; CH4 back up to 60% | 25 |  |  |  |  | 5
26 | 1126.6576 | 61.1 | 164 | 26 | 389.9591 | 2631.487 | 26 | 5.12 | 7.21 | 26 |  | 0.76333 | 26 | 2308.3333 |  | 1566.6667 | 5441.6667 | 2875 | 2191.6667 | 7 | 0 | 290557 | 2881 |  | 26
27 | 1129.258 | 60.5 | 198 | 27 | 385.2417 | 2638.8564 | 27 | 5.15 | 7.2 | 27 |  |  | 27 | [6 empty] | 8 | 0 | 291757 | 2890 | Conveyer 2 tripped breaker; truck blew radiator hose so Osha manure not delivered | 27 |  |  | 3
28 | 1080.7742 | 60.2 | 272 | 28 | 400.5161 | 2378.3226 | 28 | 5.23 | 7.15 | 28 |  |  | 28 | [6 empty] | 7 | 0 | 292857 | 2897 | Conveyer 2 tripped breaker; manual test of flare was OK | 28 |  |  | 3
29 | 1162.56 | 60.9 | 149 | 29 | 460.8 | 2598.72 | 29 | 5.41 | 7.19 | 29 |  |  | 29 | [6 empty] | 7 | 0 | 293957 | 2904 |  | 29
30 | 976.3597 | 59.5 | 265 | 30 | 409.3401 | 2116.6642 | 30 | 5.53 | 7.18 | 30 |  | 0.63667 | 30 |  |  |  | 5433.3333 | 3008.3333 | 1908.3333 | 6 | 0 | 294957 | 2910 | Genset tripped & reset; flare fired 6x; conveyer 2 breaker tripped | 30 | 1 |  | 3
average | 1031.5858 | 59.0741 | 315.8148 | average | 492.4338 | 2815.464 |  | 5.21 | 7.1229 |  |  | 0.8 | average | 2284.375 |  | 1486.9167 | 5373.9583 | 2770.8333 | 2179.1667
SD | 214.4544 | 1.8133 | 109.0289 | SD | 99.809 | 590.8498 |  | 0.15076 | 0.056315 |  |  | 0.053645 | SD | 438.9642 |  | 380.5521 | 268.2759 | 99.6522 | 176.7112

## Jul'15
VTCAD July 2015 Operational Data
notes | Day of July 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
Genset tripped overnight 6/30 & flare fired x6; conveyer 2 breaker tripped | 1 | 580.5339 | 58.5 | 161 | 1 | 451.4168 | 1244.846 | 1 | 5.45 | 7.23 | 1 |  |  | 1 | [6 empty] | 4 | 6 | 295557 | 2914
Conveyer 2 breaker tripped | 2 | 1088.0447 | 58.3 | 146 | 2 | 418.324 | 2340 | 2 | 5.21 | 7.19 | 2 |  | 0.77333 | 2 | 2916.6667 |  | 2000 | 5583.3333 | 2950 | 2483.3333 | 7 | 0 | 296657 | 2921
Calibrated gas analyzer | 3 | 1255.3086 | 59.5 | 165 | 3 | 409.8765 | 2711.1111 | 3 | 5.48 | 7.2 | 3 |  |  | 3 | [6 empty] | 8 | 0 | 297957 | 2929
Conveyer 2 breaker tripped | 4 | 1168 | 60.5 | 243 | 4 | 436.2667 | 2422.4 | 4 | 5.45 | 7.18 | 4 |  |  | 4 | [6 empty] | 7 | 0 | 298957 | 2936
Conveyer 2 breaker tripped | 5 | 1046.6438 | 60 | 248 | 5 | 418.0645 | 2221.7708 | 5 | 5.47 | 7.13 | 5 |  |  | 5 | [6 empty] | 7 | 0 | 300057 | 2943
| 6 | 1135.4395 | 59.3 | 299 | 6 | 408.3014 | 2422.2075 | 6 | 5.53 | 7.16 | 6 |  |  | 6 | [6 empty] | 8 | 0 | 301257 | 2951
genset tripped; flare fired x5; conveyer 2 breaker tripped | 7 | 513 | 57.6 | 347 | 7 | 401 | 1096 | 7 | 5.58 | 7.14 | 7 |  | 0.78 | 7 |  |  |  | 5500 | 2900 | 2275 | 4 | 5 | 301857 | 2954
| 8 | 940 | 57.7 | 321 | 8 | 464 | 1965 | 8 | 5.58 | 7.13 | 8 |  |  | 8 | [6 empty] | 6 | 0 | 302757 | 2960
genset failed to start (min-max temp?); flare fired x4; called 2G: recommended lowering temperature in genset bay; plug in pipe from prep to hydrolyzer removed; 4:45 odor alert from farm crew - AD crew did not detect odor | 9 | 449.3617 | 56.2 | 265 | 9 | 460.5957 | 924.2553 | 9 | 5.57 | 7.13 | 9 |  | 0.85 | 9 | 4483.3333 |  | 3441.6667 | 5633.3333 | 2783.3333 | 2366.6667 | 3 | 4 | 303257 | 2963
Conveyer 2 breaker tripped | 10 | 936.8436 | 57.7 | 288 | 10 | 483.3081 | 1972.929 | 10 | 5.55 | 7.13 | 10 |  |  | 10 | [6 empty] | 7 | 0 | 304157 | 2969
| 11 | 955.2286 |  |  | 11 | 581.1531 | 2067.9125 | 11 |  |  | 11 |  |  | 11 | [6 empty] | 7 | 0 | 305157 | 2976
| 12 | 1102.9196 | 58.9 | 335 | 12 | 490.8039 | 2378.0836 | 12 |  |  | 12 |  |  | 12 | [6 empty] | 8 | 0 | 306357 | 2983
Dimmick driver lost hose in prep pit; Dan K injured shoulder responding | 13 | 1123.5556 | 59.1 | 338 | 13 | 354.3704 | 2403.5556 | 13 | 5.63 | 7.08 | 13 |  |  | 13 | [6 empty] | 7 | 0 | 307357 | 2990
| 14 | 1009.32 | 63.4 | 197 | 14 | 499.9 | 2801 | 14 | 5.58 | 7.22 | 14 |  | 0.62333 | 14 | 4150 |  | 3287.5 | 5216.6667 | 3033.3333 | 1891.6667 | 8 | 0 | 308557 | 2998
| 15 | 809.3062 | 63.7 | 154 | 15 | 500.5 | 2956 | 15 | 5.45 | 7.26 | 15 |  |  | 15 | [6 empty] | 7 | 0 | 309357 | 3007
| 16 | 717.4737 | 62.9 | 244 | 16 | 512.3368 | 2723.3684 | 16 | 5.52 | 7.29 | 16 |  |  | 16 | [6 empty] | 7 | 0 | 310057 | 3015
| 17 | 556.9061 | 62.4 | 169 | 17 | 401.768 | 2057.5691 | 17 | 5.31 | 7.29 | 17 |  |  | 17 | [6 empty] | 6 | 0 | 310657 | 3021
| 18 | 778.1122 | 61.4 | 195 | 18 | 528.9193 | 2544.1313 | 18 |  |  | 18 |  |  | 18 | [6 empty] | 8 | 0 | 311457 | 3029
| 19 | 1061.3706 | 60.2 | 187 | 19 | 408.8392 | 2367.4406 | 19 |  |  | 19 |  |  | 19 | [6 empty] | 6 | 0 | 312457 | 3036
Calibrated gas analyzer; leak from feedstock storage tank 1 noted | 20 | 1099.9149 | 60.2 | 203 | 20 | 424.8511 | 2417.3617 | 20 | 5.09 | 7.3 | 20 |  |  | 20 | [6 empty] | 7 | 0 | 313557 | 3043
| 21 | 1090.29 | 61.5 | 91 | 21 | 553.5 | 2451 | 21 | 5.1 | 7.39 | 21 |  | 0.4775 | 21 | 4375 |  | 3150 | 5687.5 | 3631.25 | 1743.75 | 7 | 0 | 314757 | 3050
| 22 |  |  |  | 22 |  |  | 22 |  |  | 22 |  |  | 22
| 23 | 995.26 | 60.5 | 61 | 23 | 451 | 2138 | 23 | 5.19 | 7.38 | 23 |  |  | 23 | [6 empty] | 13 | 0 | 316757 | 3063
Seals in pump 5 (hydrolyzer to AD) leaking & need to be replaced: water in pump oil. Pump 6 (AD vertical mixing) not responding; reset controller. Pump 6 may be related to Dining hall circuit breaker overload yesterday? | 24 | 937.0777 | 60.3 | 105 | 24 | 426.9708 | 2017.8475 | 24 | 5.1 | 7.26 | 24 |  | 0.42333 | 24 | 5516.6667 |  | 4083.3333 | 7400 | 5041.6667 | 2133.3333 | 6 | 0 | 317657 | 3069
| 25 | 1060.587 | 59.8 | 57 | 25 | 657.5836 | 2296.1365 | 25 | 5.22 | 7.28 | 25 |  |  | 25 | [6 empty] | 7 | 0 | 318757 | 3076
| 26 | 838.8252 | 60.4 | 20 | 26 | 637.4266 | 1806.5455 | 26 | 5.31 | 7.3 | 26 |  |  | 26 | [6 empty] | 6 | 0 | 314557 | 3082
| 27 | 1022.6526 | 59.8 | 71 | 27 | 680.0842 | 2186.7789 | 27 | 5.3 | 7.33 | 27 |  |  | 27 | [6 empty] | 7 | 0 | 320657 | 3088
| 28 | 1049.3771 | 58.8 | 46 | 28 | 661.6477 | 2241.5003 | 28 | 5.16 | 7.34 | 28 |  | 0.45 | 28 | 5775 |  | 4200 | 6937.5 | 4666.6667 | 2100 | 7 | 0 | 321757 | 3095
| 29 | 924.4221 | 59.6 | 79 | 29 | 629.5477 | 1978.191 | 29 | 5.14 | 7.24 | 29 |  |  | 29 | [6 empty] | 7 | 0 | 322757 | 31023
| 30 | 827.4286 | 58.9 | 98 | 30 | 561.1429 | 1765.7143 | 30 | 5.11 | 7.29 | 30 |  | 0.46 | 30 | 5950 |  | 4466.6667 | 7916.6667 | 5233.3333 | 2416.6667 | 5 | 0 | 323457 | 3106
| 31 | 880 | 58.5 | 60 | 31 | 653 | 1881 | 31 | 5.24 | 7.23 | 31 | [9 empty] | 6 | 0 | 324357 | 3112
| average | 931.7735 | 59.8483 | 179.069 | average | 493.5689 | 2159.9885 |  | 5.3585 | 7.2346 |  |  | 0.62536 | average | 4536.1111 |  | 3360.4167 | 5994.0476 | 3572.3214 | 2141.9643
| SD | 203.7596 | 1.7689 | 99.2295 | SD | 91.4052 | 466.6218 |  | 0.1851 | 0.083725 |  |  | 0.17781 | SD | 1029.2482 |  | 791.7621 | 827.444 | 923.0701 | 260.6983
3

## Aug'15
VTCAD August 2015 Operational Data
notes | Day of Aug 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 914.7 | 58.4 | 54 | 1 | 661.1831 | 1966.3099 | 1 | 4.99 | 7.35 | 1 |  |  | 1 | [6 empty] | 6 | 0 | 325257 | 3118
| 2 | 1047.64 | 59.6 | 58 | 2 | 682.3693 | 2261.8537 | 2 | 5.01 | 7.32 | 2 |  |  | 2 | [6 empty] | 7 | 0 | 326357 | 3125
gas analzyer calibrated | 3 | 896.7492 | 59.8 | 217 | 3 | 596.2274 | 1945.6856 | 3 | 5.13 | 7.32 | 3 |  |  | 3 | [6 empty] | 7 | 0 | 327257 | 3131
| 4 | 1042.72 | 60.5 | 114 | 4 | 569.2 | 2237 | 4 |  |  | 4 |  |  | 4 | [6 empty] | 6 | 0 | 328357 | 3137
| 5 | 1062.72 | 60.2 | 129 | 5 | 698.9 | 2297 | 5 | 4.97 | 7.33 | 5 |  | 0.48 | 5 | 5019 |  | 3339 | 6888 | 4382 | 2107 | 5 | 0 | 329457 | 3145
| 6 | 1026.72 | 60.6 | 73 | 6 | 693.1 | 2422 | 6 | 4.96 | 7.44 | 6 |  |  | 6 | [6 empty] | 7 | 0 | 330457 | 3152
| 7 | 882.26 | 61.1 | 82 | 7 | 756.2 | 1943 | 7 | 5.03 | 7.31 | 7 |  |  | 7 | [6 empty] | 6 | 0 | 331357 | 3158
| 8 | 987.99 | 59.1 | 31 | 8 | 612.1 | 2106 | 8 | 5.05 | 7.31 | 8 |  |  | 8 | [6 empty] | 7 | 0
| 9 | 1127.66 | 59.4 | 59 | 9 | 680.5 | 2399 | 9 | 5.03 | 7.28 | 9 |  |  | 9 | [6 empty] | 7 | 0 | 333557 | 3171
| 10 | 900.25 | 59 | 51 | 10 | 694.5 | 1940 | 10 | 5.18 | 7.32 | 10 |  |  | 10 | [6 empty] | 6 | 0 | 334357 | 3177
| 11 | 1088.22 | 58.8 | 122 | 11 | 698.6 | 2342 | 11 | 5.04 | 7.43 | 11 |  | 0.435 | 11 | 5155.5 |  | 3349.5 | 6877.5 | 4588.5 | 1984.5 | 7 | 0 | 335457 | 3184
| 12 | 1204.44 | 59.8 | 79 | 12 | 757.9 | 2576 | 12 | 4.9 | 7.32 | 12 |  |  | 12 | [6 empty] | 7 | 0 | 336857 | 3192
| 13 |  |  |  | 13 |  |  | 13 |  |  | 13 |  |  | 13
gas analzyer calibrated | 14 | 1128.28 | 60.4 | 221 | 14 | 700.9 | 2594 | 14 | 4.98 | 7.31 | 14 |  |  | 14 | [6 empty] | 15 | 0 | 339057 | 3207
| 15 | 1196.15 | 60.4 | 106 | 15 | 669.5 | 2665 | 15 |  |  | 15 |  |  | 15 | [6 empty] | 7 | 0 | 340257 | 3215
| 16 | 1395.31 | 61 | 60 | 16 | 614.7 | 3069 | 16 | 4.99 | 7.32 | 16 |  |  | 16 | [6 empty] | 8 | 0 | 341657 | 3224
| 17 | 1218.61 | 61.9 | 47 | 17 | 563.4 | 3093 | 17 | 5.07 | 7.33 | 17 |  | 0.41 | 17 | 4893 |  | 3517.5 | 6562.5 | 4445 | 1837.5 | 8 | 0 | 342857 | 3233
| 18 | 1445.02 | 60.2 | 145 | 18 | 728 | 3258 | 18 | 4.96 | 7.36 | 18 |  |  | 18 | [6 empty] | 9 | 0 | 344357 | 3243
| 19 | 1583.8 | 60.4 | 165 | 19 | 646.6 | 3365 | 19 | 4.9 | 7.3 | 19 |  |  | 19 | [6 empty] | 8 | 0 | 345957 | 3253
| 20 | 1446.04 | 60.4 | 178 | 20 | 584.1 | 3059 | 20 |  |  | 20 |  |  | 20 | [6 empty] | 8 | 0 | 347457 | 3262
| 21 | 1467.71 | 60.2 | 132 | 21 | 598.2 | 3495 | 21 | 5.04 | 7.32 | 21 |  |  | 21 | [6 empty] | 9 | 0 | 348957 | 3271
| 22 | 1485.85 | 60.3 | 156 | 22 | 621 | 3169 | 22 | 5 | 7.31 | 22 |  |  | 22 | [6 empty] | 8 | 0 | 350457 | 3280
| 23 | 1374.05 | 60.9 | 207 | 23 | 603.6 | 3062 | 23 | 5.305 | 7.35 | 23 |  |  | 23 | [6 empty] | 8 | 0 | 351757 | 3290
| 24 | 1422.64 | 61.3 | 281 | 24 | 580.6 | 3137 | 24 |  | 7.52 | 24 |  | 0.43 | 24 |  |  |  | 6699 | 4515 | 1953 | 9 | 0 | 353257 | 3299
| 25 | 1452.58 | 60.7 | 201 | 25 | 635.1 | 3101 | 25 | 4.92 | 7.31 | 25 |  |  | 25 | [6 empty] | 8 | 0 | 354657 | 3308
| 26 | 1563.74 | 60.5 | 175 | 26 | 652.6 | 3344 | 26 | 4.87 | 7.35 | 26 |  |  | 26 | [6 empty] | 8 | 0 | 356257 | 3318
| 27 | 1445.01 | 60 | 167 | 27 | 585.6 | 3091 | 27 | 4.9 | 7.34 | 27 |  |  | 27 | [6 empty] | 8 | 0 | 357757 | 3327
| 28 | 1431.9 |  |  | 28 | 600.5 | 3079 | 28 |  |  | 28 |  |  | 28 | [6 empty] | 8 | 0 | 359157 | 3336
| 29 | 587.65 | 60.9 | 164 | 29 | 656.8 | 1256 | 29 | 4.93 | 7.28 | 29 |  |  | 29 | [6 empty] | 4 | 4 | 359757 | 3340
| 30 | 1257.67 | 61.9 | 35 | 30 | 613.6 | 3478 | 30 | 5.07 | 7.26 | 30 |  |  | 30 | [6 empty] | 8 | 1 | 361057 | 3350
| 31 | 1822.99 | 62.6 | 1 | 31 | 639.7 | 3808 | 31 | 5.07 | 7.43 | 31 |  | 0.535 | 31 | 6025 |  | 4262.5 | 8537.5 | 5375 | 2862.5 | 8 | 0 | 362157 | 3361
| average | 1230.2356 | 60.275 | 125.3214 | average | 646.7441 | 2718.6283 |  | 5.0094 | 7.3356 |  |  | 0.43875 | average | 5022.5 |  | 3402 | 6756.75 | 4482.625 | 1970.5
| SD | 270.2074 | 0.84399 | 66.6389 | SD | 55.1007 | 605.4415 |  | 0.097916 | 0.055157 |  |  | 0.029545 | SD | 131.285 |  | 100.1636 | 155.8581 | 89.0668 | 110.7903

## Sep'15
VTCAD September 2015 Operational Data
notes | Day of Sep 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 1217.62 | 59.4 | 304 | 1 | 604.3 | 4470 | 1 | 4.9 | 7.27 | 1 |  |  | 1 | [6 empty] | 9 | 0 | 363457 | 3374
| 2 | 1830.08 | 60.8 | 193 | 2 | 617.9 | 4745 | 2 | 4.83 | 7.28 | 2 |  |  | 2 | [6 empty] | 9 | 0 | 365457 | 3389
| 3 | 1704.88 | 62.2 | 119 | 3 | 510.7 | 4538 | 3 | 4.88 | 7.25 | 3 |  |  | 3 | [6 empty] | 7 | 0 | 366957 | 3041
genset off during night | 4 | 943.22 | 63.4 | 76 | 4 | 650.7 | 2383 | 4 | 4.77 | 7.28 | 4 |  |  | 4 | [6 empty] | 4 | 1 | 367957 | 3408
genset off during night | 5 | 3023.25 | 64.3 | 159 | 5 | 599.7 | 777 | 5 | 4.77 | 7.23 | 5 |  |  | 5 | [6 empty] | 4 | 1 | 368757 | 3416
genset off during night | 6 | 1304.48 | 65.5 | 51 | 6 | 647.4 | 4864 | 6 | 4.8 | 7.22 | 6 |  |  | 6 | [6 empty] | 7 | 1 | 370157 | 3430
| 7 | 1521.46 | 65.5 | 149 | 7 | 636.7 | 5491 | 7 | 5.04 | 7.15 | 7 |  | 0.61 | 7 | 5350 |  | 3912.5 | 6900 | 4137.5 | 2500 | 8 | 2 | 371757 | 3446
genset down briefly | 8 | 1457.44 | 65.7 | 133 | 8 | 532 | 5532 | 8 | 4.93 | 7.18 | 8 |  |  | 8 | [6 empty] | 5 | 9 | 373057 | 3461
genset problems | 9 | 1397.12 | 65.6 | 159 | 9 | 597.3 | 5383 | 9 |  |  | 9 |  |  | 9 | [6 empty] | 5 | 24 | 374557 | 3476
| 10 |  |  |  | 10 |  |  | 10 |  |  | 10 |  |  | 10
genset problems | 11 | 815.59 | 65.6 | 46 | 11 | 631.7 | 2844 | 11 | 4.73 | 7.12 | 11 |  |  | 11 | [6 empty] | 6 | 60 | 376257 | 3492
| 12 |  | 64.4 | 132 | 12 |  |  | 12 | 4.88 | 7.4 | 12 |  | 0.62333 | 12 | 4808.3333 |  | 3258.3333 | 6041.6667 | 3541.6667 | 2216.6667
genset offline | 13 | 402.51 | 63.9 | 168 | 13 | 603.8 | 1526 | 13 | 4.92 | 7.08 | 13 |  |  | 13 | [6 empty] | 3 | 77 | 377057 | 3501
genset offline | 14 | 0 |  |  | 14 | 528.1 | 0 | 14 | 4.88 | 7.12 | 14 |  |  | 14 | [6 empty] | 0 | 39 | 377057 | 3501
genset offline | 15 | 0 |  |  | 15 | 627.4 | 0 | 15 | 4.92 | 7.13 | 15 |  |  | 15 | [6 empty] | 0 | 43 | 377057 | 3501
genset offline | 16 | 0 |  |  | 16 | 662.1 | 0 | 16 | 4.87 |  | 16 |  | 0.5 | 16 | 5125 |  | 3775 | 6162.5 | 3900 | 1950 | 0 | 42 | 377057 | 3501
genset offline | 17 | 0 |  |  | 17 | 618.9 | 0 | 17 | 4.92 | 7.11 | 17 |  |  | 17 | [6 empty] | 0 | 40 | 377057 | 3501
restarted genset 15:30, manually emptied flare water trap | 18 | 0 |  |  | 18 | 687.6 | 0 | 18 | 5.06 | 7.12 | 18 |  |  | 18 | [6 empty] | 0 | 39 | 377057 | 3501
| 19 | 791.76 | 62.2 | 72 | 19 | 642.4 | 3031 | 19 | 5.02 | 7.09 | 19 |  |  | 19 | [6 empty] | 6 | 11 | 377857 | 3509
| 20 | 1178.9 | 63 | 208 | 20 | 620.4 | 4397 | 20 | 5.15 | 7.01 | 20 |  |  | 20 | [6 empty] | 9 | 0 | 379057 | 3522
| 21 | 1318.66 | 64.5 | 18 | 21 | 640.8 | 4838 | 21 | 5.08 |  | 21 |  |  | 21 | [6 empty] | 7 | 0 | 380357 | 3536
| 22 | 1363.49 | 64.9 | 118 | 22 | 638.3 | 5043 | 22 | 5.16 | 6.98 | 22 |  | 0.63 | 22 | 5400 |  | 4175 | 5775 | 3387.5 | 2137.5 | 7 | 0 | 381757 | 3550
| 23 | 1330.14 | 64.6 | 73 | 23 | 655.3 | 4887 | 23 | 5.13 | 7.06 | 23 |  |  | 23 | [6 empty] | 8 | 0 | 383057 | 3564
| 24 | 1437.97 | 65.1 | 7 | 24 | 596.3 | 5334 | 24 |  |  | 24 |  |  | 24 | [6 empty] | 7 | 0 | 384557 | 3579
| 25 | 1484.44 | 64.2 | 15 | 25 | 600.4 | 5298 | 25 | 5.14 | 6.92 | 25 |  |  | 25 | [6 empty] | 7 | 0 | 386157 | 3595
| 26 | 1541.51 | 64.8 | 7 | 26 | 546.3 | 5624 | 26 | 4.98 | 7.04 | 26 |  |  | 26 | [6 empty] | 7 | 0 | 387657 | 3610
| 27 | 1664.16 | 63.5 | 13 | 27 | 596.8 | 6220 | 27 | 4.98 | 7 | 27 |  |  | 27 | [6 empty] | 7 | 0 | 389457 | 3629
| 28 | 1510.09 | 65.2 | 60 | 28 | 513.3 | 5546 | 28 | 4.97 |  | 28 |  |  | 28 | [6 empty] | 8 | 5 | 390957 | 3644
| 29 | 1470.25 | 63.4 | 43 | 29 | 554.2 | 5688 | 29 | 4.99 | 6.98 | 29 |  |  | 29 | [6 empty] | 7 | 0 | 392357 | 3659
| 30 | 1554.26 | 64.4 | 76 | 30 | 687.4 | 6140 | 30 | 5.02 | 7.21 | 30 |  |  | 30 | [6 empty] | 7 | 0 | 393957 | 3677
| average | 1152.26 | 64.0042 | 99.9583 | average | 608.8643 | 3735.6786 |  | 4.9526 | 7.1346 |  |  | 0.59083 | average | 5170.8333 |  | 3780.2083 | 6219.7917 | 3741.6667 | 2201.0417
| SD | 698.4341 | 1.5815 | 75.2852 | SD | 48.8006 | 2205.3846 |  | 0.12088 | 0.1174 |  |  | 0.061124 | SD | 269.6448 |  | 385.4617 | 481.5025 | 340.1899 | 228.5313

## Oct'15
VTCAD October 2015 Operational Data
notes | Day of Oct 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
33.3108 | 1 | 775.38 | 65.8 | 84 | 1 | 642.5 | 2958 | 1 | 5.04 | 7.21 | 1 |  | 0.55035 | 1 | 5216.6667 |  | 3791.6667 | 6008.3333 | 3625 | 1991.6667 | 3 | 22 | 394757 | 3685
70.1914 | 2 | 1885.89 | 64.6 | 103 | 2 | 663.7 | 6233 | 2 | 4.98 | 7.05 | 2 |  |  | 2 | [6 empty] | 6 | 0 | 396757 | 3704
67.9167 | 3 | 1596.06 | 64.5 | 65 | 3 | 616.1 | 6031 | 3 |  |  | 3 |  |  | 3 | [6 empty] | 6 | 0 | 398357 | 3720
64.9099 | 4 | 1508.72 | 63.3 | 63 | 4 | 607.9 | 5764 | 4 | 4.87 | 7.14 | 4 |  |  | 4 | [6 empty] | 7 | 0 | 399857 | 3736
69.7635 | 5 | 1763.71 | 63.5 | 182 | 5 | 646.4 | 6195 | 5 | 4.87 | 7.22 | 5 |  |  | 5 | [6 empty] | 7 | 0 | 401657 | 3753
64.6847 | 6 | 1892.72 | 64 | 174 | 6 | 587.1 | 5744 | 6 | 4.89 | 7.05 | 6 |  |  | 6 | [6 empty] | 7 | 0 | 403557 | 3769
62.6239 | 7 | 1826.14 | 63.2 | 200 | 7 | 629.2 | 5561 | 7 | 4.85 | 7.03 | 7 |  |  | 7 | [6 empty] | 8 | 0 | 405557 | 3786
| 8 | 1433.2919 | 63.6 | 188 | 8 | 541.118 | 4842.1118 | 8 | 5.04 | 7.12 | 8 |  |  | 8 | [6 empty] | 7 | 0 | 406857 | 3799
| 9 | 1476.8485 | 63.3 | 190 | 9 | 613.8182 | 4706.9091 | 9 | 5.09 | 7.32 | 9 |  | 0.52755 | 9 | 5387.5 |  | 4212.5 | 6387.5 | 3862.5 | 2037.5 | 8 | 0 | 408457 | 3813
| 10 | 1379.52 | 62.6 | 252 | 10 | 655.68 | 3916.8 | 10 | 5.37 | 7.15 | 10 |  |  | 10 | [6 empty] | 8 | 0 | 409857 | 3825
| 11 | 912.8571 | 62.9 | 230 | 11 | 567.6923 | 3404.1758 | 11 | 5.48 | 7.06 | 11 |  |  | 11 | [6 empty] | 7 | 0 | 410857 | 3835
| 12 | 983.6242 | 60.9 | 242 | 12 | 564.8322 | 3052.8859 | 12 | 5.6 | 7.08 | 12 |  |  | 12 | [6 empty] | 7 | 0 | 411757 | 3843
| 13 | 1432.9263 | 58.4 | 315 | 13 | 599.2421 | 3351.9158 | 13 | 5.58 | 7.13 | 13 |  |  | 13 | [6 empty] | 7 | 0 | 413257 | 3853
| 14 | 1457.7656 | 61.6 | 265 | 14 | 603.0432 | 3124.7704 | 14 | 5.58 | 7.2 | 14 |  |  | 14 | [6 empty] | 8 | 0 | 414757 | 3862
| 15 | 1316.9145 | 61.1 | 261 | 15 | 583.4051 | 2963.0577 | 15 | 5.57 | 7.07 | 15 |  |  | 15 | [6 empty] | 7 | 0 | 416057 | 3871
| 16 | 1285.5061 | 60.4 | 270 | 16 | 583.9676 | 2874.17 | 16 | 5.59 | 7.21 | 16 |  | 0.46538 | 16 | 6600 |  | 5312.5 | 7012.5 | 4462.5 | 2075 | 7 | 0 | 417457 | 3879
| 17 | 1419.2806 | 61 | 277 | 17 | 576 | 3086.1583 | 17 | 5.6 | 7.18 | 17 |  |  | 17 | [6 empty] | 8 | 0 | 418757 | 3888
| 18 | 956.5102 | 62.5 | 240 | 18 | 683.3576 | 2779.1143 | 18 | 5.55 | 7.4 | 18 |  |  | 18 | [6 empty] | 6 | 0 | 419857 | 3897
| 19 | 788.7387 | 63 | 259 | 19 | 585.0314 | 3044.5714 | 19 | 5.93 | 7.23 | 19 |  |  | 19 | [6 empty] | 7 | 0 | 420657 | 3905
| 20 | 1003.8615 | 61.2 | 233 | 20 | 661.1054 | 3415.888 | 20 | 5.42 | 7.14 | 20 |  |  | 20 | [6 empty] | 7 | 0 | 421557 | 3915
| 21 | 1312.7671 | 61.7 | 216 | 21 | 634.1918 | 3191.6712 | 21 | 5.7 | 7.16 | 21 |  |  | 21 | [6 empty] | 8 | 0 | 422957 | 3924
| 22 | 1328.4362 | 61.5 | 198 | 22 | 628.0631 | 3374.8063 | 22 | 5.83 | 7.17 | 22 |  |  | 22 | [6 empty] | 7 | 0 | 424257 | 3934
| 23 | 1242.7884 | 60.4 | 197 | 23 | 702.6774 | 3007.0327 | 23 | 5.83 | 7.18 | 23 |  |  | 23 | [6 empty] | 8 | 0 | 425657 | 3944
| 24 | 1213.5081 | 60.1 | 175 | 24 | 564.0093 | 2958.8281 | 24 | 5.73 | 7.1 | 24 |  |  | 24 | [6 empty] | 6 | 0 | 426857 | 3952
| 25 | 1336.3522 | 61.3 | 148 | 25 | 561.5094 | 3337.8616 | 25 | 5.75 | 7.17 | 25 |  |  | 25 | [6 empty] | 8 | 0 | 428057 | 3961
| 26 | 1124.9409 | 61.3 | 170 | 26 | 574.297 | 3143.9685 | 26 | 5.8 |  | 26 |  |  | 26 | [6 empty] | 7 | 0 | 429257 | 3971
| 27 | 1246.7045 | 60 | 250 | 27 | 639.2045 | 2992.5 | 27 | 5.65 | 7.14 | 27 |  | 0.4372 | 27 | 6087.5 |  | 4887.5 | 7837.5 | 5175 | 2262.5 | 7 | 0 | 430997 | 3980
| 28 | 1534.9677 | 60.1 | 224 | 28 | 582.1935 | 3577.8065 | 28 | 5.69 | 7.2 | 28 |  |  | 28 | [6 empty] | 7 | 0 | 432057 | 3990
| 29 | 1727.8001 | 61 | 147 | 29 | 646.551 | 3759.3893 | 29 | 5.55 | 7.16 | 29 |  |  | 29 | [6 empty] | 8 | 2 | 433757 | 4001
| 30 | 1796.1186 | 62.5 | 137 | 30 | 582.2102 | 3795.0404 | 30 | 5.72 |  | 30 |  |  | 30 | [6 empty] | 8 | 0 | 435657 | 4012
| 31 | 2055.46 | 60.9 | 140 | 31 | 586 | 4477 | 31 | 5.37 | 7.26 | 31 |  |  | 31 | [6 empty] | 9 | 0 | 437757 | 4025
| average | 1387.6164 | 62.0065 | 196.6129 | average | 610.0678 | 3892.4011 | [5 empty] | 0.49512 | average | 5822.9167 |  | 4551.0417 | 6811.4583 | 4281.25 | 2091.6667
| SD | 330.9684 | 1.6371 | 63.8324 | SD | 39.8954 | 1134.7339 |  | 5.4507 | 7.1618 |  |  | 0.052727 | SD | 640.57 |  | 679.2849 | 799.5686 | 692.2563 | 118.8779
[9 empty] | 0.3334 | 0.082509

## Nov'15
VTCAD November 2015 Operational Data
notes | Day of Nov 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 1691.8631 | 64 | 52 | 1 | 585.8555 | 5015.3612 | 1 | 5.21 | 7.28 | 1 |  |  | 1 | [6 empty] | 7 | 0 | 439357 | 4038
Pierre called but agreed that odor was due to spreading effluent on field 31 (Fire House field). Hydrolyzer slurry was thick. | 2 | 2653 | 64.7 | 174 | 2 | 562 | 4320 | 2 | 5.19 | 7.12 | 2 |  |  | 2 | [6 empty] | 8 | 0 | 440457 | 4051
Stong ammonia in prep pit at 7:45 am - 9 am. Fished rubber roofing chunks out of the prep pit. Purged bottom of AD tank. | 3 | 1337.6944 | 64.9 | 163 | 3 | 580.0536 | 5023.5925 | 3 | 5.23 | 7.16 | 3 |  |  | 3 | [6 empty] | 8 | 0 | 441857 | 4065
| 4 | 1258.3976 | 64.1 | 174 | 4 | 568.3086 | 4878.6944 | 4 | 5.12 | 7.04 | 4 |  |  | 4 | [6 empty] | 7 | 0 | 443057 | 4078
H2S levels increased to 580 ppm so FeCl3 increased. Ammonia from prep pit. | 5 | 1279.6981 | 64.2 | 248 | 5 | 625.8113 | 4998.3396 | 5 | 5.19 | 7.06 | 5 |  | 0.45 | 5 | 7400 |  | 5775 | 8050 | 5200 | 2325 | 8 | 0 | 444557 | 4094
| 6 | 1877.6575 | 62.7 | 234 | 6 | 552.9429 | 5366.1082 | 6 | 5.01 | 7.24 | 6 |  |  | 6 | [6 empty] | 7 | 0 | 446257 | 4108
| 7 | 2075.4023 | 61.8 | 584 | 7 | 602.2989 | 5133.7931 | 7 | 4.95 | 7.58 | 7 |  |  | 7 | [6 empty] | 9 | 0 | 448457 | 4123
| 8 | 1418.6667 | 62.5 | 430 | 8 | 580.2667 | 4464 | 8 | 5.17 | 7.29 | 8 |  |  | 8 | [6 empty] | 8 | 0 | 449957 | 4136
| 9 | 1188.7912 | 62.5 | 430 | 9 | 540 | 4466.3736 | 9 | 5.04 | 7.02 | 9 |  |  | 9 | [6 empty] | 7 | 0 | 451157 | 4149
2G present for genset maintenance. | 10 | 1125.6697 | 61.7 | 244 | 10 | 526.6052 | 4054.6563 | 10 | 5.1 | 7.09 | 10 |  | 0.44 | 10 | 6350 |  | 4962.5 | 7437.5 | 4937.5 | 2162.5 | 7 | 10 | 452257 | 4161
| 11 | 1733.0458 | 63 | 179 | 11 | 644.3127 | 4930.3504 | 11 | 5.17 | 7.02 | 11 |  |  | 11 | [6 empty] | 8 | 0 | 454057 | 4175
| 12 | 1276.8831 | 64.3 | 206 | 12 | 572.4675 | 4482.0779 | 12 | 5.35 | 7.17 | 12 |  |  | 12 | [6 empty] | 7 | 0 | 455357 | 4188
| 13 | 1271.0452 | 63 | 201 | 13 | 565.1247 | 4533.621 | 13 | 5.11 | 7.01 | 13 |  |  | 13 | [6 empty] | 9 | 0 | 456657 | 4201
| 14 | 1524.3429 | 62.7 | 170 | 14 | 551.3143 | 4147.2 | 14 | 5.04 | 6.98 | 14 |  |  | 14 | [6 empty] | 7 | 0 | 458157 | 4213
| 15 | 1082 | 62.7 | 125 | 15 | 613 | 4276 | 15 | 5.17 | 7.1 | 15 |  |  | 15 | [6 empty] | 8 | 0 | 459257 | 4225
| 16 | 1171.0544 | 63.4 | 270 | 16 | 548.8077 | 4606.8091 | 16 | 5.38 | 7.08 | 16 |  |  | 16 | [6 empty] | 7 | 0 | 460457 | 4238
| 17 | 1316.25 | 63.4 | 112 | 17 | 631.0227 | 5121.8182 | 17 | 5.48 | 7.05 | 17 | 13.1659 | 0.45118 | 17 | 6425 | 387.5 | 4762.5 | 7325 | 4737.5 | 2137.5 | 8 | 0 | 461757 | 4252
| 18 | 1366.5503 | 64.3 | 167 | 18 | 589.5302 | 5384.0537 | 18 | 5.58 | 7.18 | 18 |  |  | 18 | [6 empty] | 7 | 0 | 463157 | 4268
| 19 | 1201.3097 | 63.8 | 263 | 19 | 597.2169 | 4706.03 | 19 | 5.53 | 7.37 | 19 |  |  | 19 | [6 empty] | 8 | 0 | 464457 | 4282
| 20 | 1198.9565 | 64.7 | 192 | 20 | 553.0435 | 4656 | 20 | 5.56 | 7 | 20 |  |  | 20 | [6 empty] | 7 | 0 | 465557 | 4295
| 21 | 1213.5051 | 63.6 | 266 | 21 | 590.6441 | 4691.9593 | 21 | 5.34 | 7.06 | 21 |  |  | 21 | [6 empty] | 7 | 0 | 466857 | 4308
| 22 | 1057.5584 | 63.7 | 267 | 22 | 543.2727 | 4017.974 | 22 | 5.4 | 7.12 | 22 |  |  | 22 | [6 empty] | 9 | 0 | 468057 | 4321
| 23 | 984.142 | 62.6 | 283 | 23 | 599.645 | 3789.5858 | 23 | 5.55 | 7.03 | 23 |  |  | 23 | [6 empty] | 6 | 0 | 468957 | 4331
| 24 | 951.7127 | 62.8 | 184 | 24 | 604.6409 | 3717.3481 | 24 | 5.56 | 7.11 | 24 |  | 0.47 | 24 | 6412.5 |  | 4975 | 8162.5 | 5150 | 2387.5 | 8 | 0 | 469957 | 4342
| 25 | 1115.6485 | 62.9 | 222 | 25 | 587.4477 | 4339.0795 | 25 | 5.45 | 7.02 | 25 |  |  | 25 | [6 empty] | 8 | 0 | 471057 | 4354
| 26 | 1588.8239 | 63.7 | 278 | 26 | 591.1903 | 5014.8539 | 26 | 5.6 | 7.18 | 26 |  |  | 26 | [6 empty] | 7 | 0 | 472657 | 4368
| 27 | 1232.2689 | 62.8 | 289 | 27 | 560.6723 | 4861.5126 | 27 | 5.57 | 7.05 | 27 |  |  | 27 | [6 empty] | 8 | 0 | 473857 | 4382
| 28 | 699.0102 | 61.1 | 353 | 28 | 658.0068 | 2275.6881 | 28 | 5.45 | 7.23 | 28 |  |  | 28 | [6 empty] | 4 | 24 | 474557 | 4389
| 29 | 1244.2817 | 64.4 | 292 | 29 | 593.2394 | 4586.7042 | 29 | 5.48 | 7.12 | 29 |  |  | 29 | [6 empty] | 7 | 0 | 475857 | 4401
| 30 | 1603.8445 | 66 | 229 | 30 | 630.9541 | 5132.0989 | 30 | 5.25 | 7.07 | 30 |  |  | 30 | [6 empty] | 6 | 1 | 477457 | 4416
| average | 1357.9692 | 63.4 | 242.7 | average | 584.9899 | 4566.3895 |  | 5.311 | 7.1224 |  |  | 0.4528 | average | 6646.875 |  | 5118.75 | 7743.75 | 5006.25 | 2253.125
| SD | 374.7484 | 1.0609 | 104.4758 | SD | 32.3821 | 614.6119 |  | 0.20277 | 0.1273 |  |  | 0.012518 | SD | 503.1541 |  | 448.2024 | 423.5883 | 212.2548 | 122.2084

## Dec'15
VTCAD December 2015 Operational Data
notes | Day of Dec 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 1845.3699 | 65.2 | 382 | 1 | 686.4658 | 5947.3973 | 1 | 5.21 | 7.1 | 1 |  |  | 1 | [6 empty] | 6 | 0 | 479357 | 4433
| 2 | 1330.2378 | 64.5 | 467 | 2 | 771.3566 | 5237.3706 | 2 | 4.99 | 7.04 | 2 |  | 0.39216 | 2 | 7112.5 |  | 5525 | 8050 | 5487.5 | 2150 | 8 | 0 | 482157 | 4463
| 3 | 1285.2973 | 63.4 | 650 | 3 | 745.2973 | 5060.4324 | 3 | 5.07 | 7.12 | 3 |  |  | 3 | [6 empty] | 8 | 0 | 482157 | 4463
| 4 | 1222.9714 | 64.2 | 394 | 4 | 601.7143 | 4658.4 | 4 | 5.07 | 7.13 | 4 |  |  | 4 | [6 empty] | 8 | 0 | 483357 | 4476
| 5 | 1337.0754 | 62 | 659 | 5 | 609.9934 | 5093.3508 | 5 | 4.97 | 7.15 | 5 |  |  | 5 | [6 empty] | 8 | 0 | 484857 | 4492
| 6 | 1342.9565 | 62.1 | 772 | 6 | 566.6087 | 5306.087 | 6 | 4.99 | 7.04 | 6 |  |  | 6 | [6 empty] | 7 | 0 | 486157 | 4506
| 7 | 1292.4382 | 64.4 | 339 | 7 | 564.8057 | 5027.2792 | 7 | 5.08 | 7.07 | 7 |  |  | 7 | [6 empty] | 7 | 0 | 487457 | 4520
| 8 | 1079.7546 | 62.6 | 443 | 8 | 701.8405 | 4118.773 | 8 | 5.01 | 7.14 | 8 |  |  | 8 | [6 empty] | 7 | 0 | 488557 | 4532
| 9 | 1440.9387 | 61.9 | 436 | 9 | 623.3116 | 4163.2334 | 9 | 4.93 | 7.15 | 9 |  |  | 9 | [6 empty] | 8 | 0 | 490057 | 4545
| 10 | 1665.1937 | 58.2 | 669 | 10 | 481.3773 | 3535.9541 | 10 | 4.78 | 7.1 | 10 |  |  | 10 | [6 empty] | 8 | 0 | 491857 | 4556
| 11 | 2612.3013 | 60.5 | 489 | 11 | 480.6634 | 5569.924 | 11 | 4.68 | 7.13 | 11 |  | 0.46 | 11 | 6975 |  | 4800 | 8500 | 5600 | 2575
| 12 | 2993.4354 | 60.8 | 581 | 12 | 474.7484 | 6437.4617 | 12 | 4.72 | 7.1 | 12 |  |  | 12 | [6 empty] | 7 | 10 | 497257 | 4588
| 13 | 2412.1519 | 64 | 312 | 13 | 465.8228 | 7149.3671 | 13 | 4.7 | 7.04 | 13 |  |  | 13 | [6 empty] | 5 | 0 | 499657 | 4608
| 14 | 1749 | 63.6 | 310 | 14 | 537 | 7026 | 14 | 4.7 | 7.01 | 14 |  |  | 14 | [6 empty] | 5 | 0 | 501457 | 4627
| 15 | 1893.551 | 63.4 | 242 | 15 | 587.7551 | 7562.449 | 15 | 4.84 | 7.13 | 15 |  |  | 15 | [6 empty] | 4 | 0 | 503497 | 4648
| 16 | 2362 | 64.3 | 200 | 16 | 489.2 | 7191.8 | 16 | 4.7 | 7.03 | 16 |  |  | 16 | [6 empty] | 5 | 0 | 505757 | 4668
| 17 | 1740.4 | 64 | 234 | 17 | 497.6 | 6861.5 | 17 | 4.76 | 7.04 | 17 |  |  | 17 | [6 empty] | 5 | 0 | 507559 | 4687
| 18 | 1945.6 | 64.1 | 138 | 18 | 574.4 | 8013.4 | 18 | 4.68 | 7.02 | 18 |  |  | 18 | [6 empty] | 3 | 0 | 509997 | 4710
Excess gas! Hurrah! | 19 | 2183.2 | 63.9 | 163 | 19 | 574.8 | 9039.3 | 19 | 4.71 | 7 | 19 |  |  | 19 | [6 empty] | 0 | 14 | 511757 | 4733
PMP08 sounded rough on start | 20 | 2561.7 | 64.9 | 102 | 20 | 620.5 | 8939.1 | 20 |  | 7.02 | 20 |  |  | 20 | [6 empty] | 0 | 29 | 514357 | 4758
Turned off EV10. Gary replaced seal on PMP05. | 21 | 2735.1 | 66.1 | 64 | 21 | 526.1 | 8277.6 | 21 | 5.05 | 7.03 | 21 |  |  | 21 | [6 empty] | 0 | 34 | 517257 | 4781
Geset oil changed. 'Squirter' heat trace short circuited. | 22 | 2559 | 65.5 | 110 | 22 | 535.5 | 8880.9 | 22 | 5.3 | 6.98 | 22 |  |  | 22 | [6 empty] | 0 | 20 | 519857 | 4805
Genset tripped & manually reset several times. | 23 | 2115.7 | 66.6 | 55 | 23 | 554.6 | 7434.6 | 23 | 5.23 | 7.02 | 23 |  |  | 23 | [6 empty] | 2 | 36 | 522057 | 4826
AD gas @ 101%. Flare working but biogas smell in parking lot. Genset tripped & manually restarted. Flare water trap emptied & was murky greenish brown. | 24 | 1226.6 | 66.4 | 121 | 24 | 547.3 | 4012.6 | 24 | 5.23 | 7.03 | 24 |  |  | 24 | [6 empty] | 3 | 85 | 523357 | 4837
time not recorded | 25 | 1734 | 64.5 | 53 | 25 | 536 | 6675 | 25 | 5.1 | 7.01 | 25 |  |  | 25 | [6 empty] | 5 | 1 | 525057 | 4856
time not recorded | 26 | 1493 | 65.4 | 110 | 26 | 506 | 5339 | 26 | 5.42 | 7.05 | 26 |  |  | 26 | [6 empty] | 6 | 0 | 526657 | 4871
| 27 | 1386.7 | 63.4 | 110 | 27 | 550.1 | 5225.7 | 27 | 5.33 | 7.1 | 27 |  |  | 27 | [6 empty] | 8 | 0 | 528057 | 4886
| 28 | 1195.2 | 63.7 | 73 | 28 | 576.8 | 4620 | 28 | 5.37 | 7.04 | 28 |  |  | 28 | [6 empty] | 8 | 0 | 529257 | 4899
Gas mix breaker tripped; restarted genset. PMP05 seal leaking, Tightened gas intake flanges. Bottom pipe from hydrolyzer to AD blocked; feeding from upper pipe. Hydrolysis slurry thick. Flare not working. | 29 | 1474 | 61.2 | 245 | 29 | 603.1 | 5247.7 | 29 | 5.22 | 7.18 | 29 |  |  | 29 | [6 empty] | 7 | 3 | 530957 | 4916
Hydrolysis slurry thick. pH probe working very slowly. | 30 | 1687 | 62.3 | 241 | 30 | 576 | 4514.3 | 30 | 5.18 | 6.99 | 30 |  |  | 30 | [6 empty] | 6 | 3 | 532457 | 4927
Smell of biogas in parking lot & 0% gas in AD. Ice & snow ripped off electrical lines to AD sensors. Electrical lines repaired. Ops back to normal, flare functioning. | 31
| average | 1796.7291 | 63.57 | 305.4667 | average | 572.2254 | 6072.1993 |  | 5.0007 | 7.0663 |  |  | 0.42608 | average | 7043.75 |  | 5162.5 | 8275 | 5543.75 | 2362.5
| SD | 536.2057 | 1.8646 | 210.5259 | SD | 76.5148 | 1589.7578 |  | 0.23502 | 0.055739 |  |  | 0.04797 | SD | 97.2272 |  | 512.6524 | 318.1981 | 79.5495 | 300.5204

## Template
VTCAD ___MONTH___ 2015 Operational Data
notes | Day of _____ 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
| 2 |  |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 2
| 3 |  |  |  | 3 |  |  | 3 |  |  | 3 |  |  | 3
| 4 |  |  |  | 4 |  |  | 4 |  |  | 4 |  |  | 4
| 5 |  |  |  | 5 |  |  | 5 |  |  | 5 |  |  | 5
| 6 |  |  |  | 6 |  |  | 6 |  |  | 6 |  |  | 6
| 7 |  |  |  | 7 |  |  | 7 |  |  | 7 |  |  | 7
| 8 |  |  |  | 8 |  |  | 8 |  |  | 8 |  |  | 8
| 9 |  |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9
| 10 |  |  |  | 10 |  |  | 10 |  |  | 10 |  |  | 10
| 11 |  |  |  | 11 |  |  | 11 |  |  | 11 |  |  | 11
| 12 |  |  |  | 12 |  |  | 12 |  |  | 12 |  |  | 12
| 13 |  |  |  | 13 |  |  | 13 |  |  | 13 |  |  | 13
| 14 |  |  |  | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 15 |  |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15
| 16 |  |  |  | 16 |  |  | 16 |  |  | 16 |  |  | 16
| 17 |  |  |  | 17 |  |  | 17 |  |  | 17 |  |  | 17
| 18 |  |  |  | 18 |  |  | 18 |  |  | 18 |  |  | 18
| 19 |  |  |  | 19 |  |  | 19 |  |  | 19 |  |  | 19
| 20 |  |  |  | 20 |  |  | 20 |  |  | 20 |  |  | 20
| 21 |  |  |  | 21 |  |  | 21 |  |  | 21 |  |  | 21
| 22 |  |  |  | 22 |  |  | 22 |  |  | 22 |  |  | 22
| 23 |  |  |  | 23 |  |  | 23 |  |  | 23 |  |  | 23
| 24 |  |  |  | 24 |  |  | 24 |  |  | 24 |  |  | 24
| 25 |  |  |  | 25 |  |  | 25 |  |  | 25 |  |  | 25
| 26 |  |  |  | 26 |  |  | 26 |  |  | 26 |  |  | 26
| 27 |  |  |  | 27 |  |  | 27 |  |  | 27 |  |  | 27
| 28 |  |  |  | 28 |  |  | 28 |  |  | 28 |  |  | 28
| 29 |  |  |  | 29 |  |  | 29 |  |  | 29 |  |  | 29
| 30 |  |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30
| average | #DIV/0! | #DIV/0! | #DIV/0! | average | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| SD | #DIV/0! | #DIV/0! | #DIV/0! | SD | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!