## Template
VTCAD ___MONTH___ 2015 Operational Data
notes | Day of _____ 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
| 2 |  |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 2
| 3 |  |  |  | 3 |  |  | 3 |  |  | 3 |  |  | 3
| 4 |  |  |  | 4 |  |  | 4 |  |  | 4 |  |  | 4
| 5 |  |  |  | 5 |  |  | 5 |  |  | 5 |  |  | 5
| 6 |  |  |  | 6 |  |  | 6 |  |  | 6 |  |  | 6
| 7 |  |  |  | 7 |  |  | 7 |  |  | 7 |  |  | 7
| 8 |  |  |  | 8 |  |  | 8 |  |  | 8 |  |  | 8
| 9 |  |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9
| 10 |  |  |  | 10 |  |  | 10 |  |  | 10 |  |  | 10
| 11 |  |  |  | 11 |  |  | 11 |  |  | 11 |  |  | 11
| 12 |  |  |  | 12 |  |  | 12 |  |  | 12 |  |  | 12
| 13 |  |  |  | 13 |  |  | 13 |  |  | 13 |  |  | 13
| 14 |  |  |  | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 15 |  |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15
| 16 |  |  |  | 16 |  |  | 16 |  |  | 16 |  |  | 16
| 17 |  |  |  | 17 |  |  | 17 |  |  | 17 |  |  | 17
| 18 |  |  |  | 18 |  |  | 18 |  |  | 18 |  |  | 18
| 19 |  |  |  | 19 |  |  | 19 |  |  | 19 |  |  | 19
| 20 |  |  |  | 20 |  |  | 20 |  |  | 20 |  |  | 20
| 21 |  |  |  | 21 |  |  | 21 |  |  | 21 |  |  | 21
| 22 |  |  |  | 22 |  |  | 22 |  |  | 22 |  |  | 22
| 23 |  |  |  | 23 |  |  | 23 |  |  | 23 |  |  | 23
| 24 |  |  |  | 24 |  |  | 24 |  |  | 24 |  |  | 24
| 25 |  |  |  | 25 |  |  | 25 |  |  | 25 |  |  | 25
| 26 |  |  |  | 26 |  |  | 26 |  |  | 26 |  |  | 26
| 27 |  |  |  | 27 |  |  | 27 |  |  | 27 |  |  | 27
| 28 |  |  |  | 28 |  |  | 28 |  |  | 28 |  |  | 28
| 29 |  |  |  | 29 |  |  | 29 |  |  | 29 |  |  | 29
| 30 |  |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30
| average | #DIV/0! | #DIV/0! | #DIV/0! | average | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| SD | #DIV/0! | #DIV/0! | #DIV/0! | SD | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Jan'16
VTCAD January 2016 Operational Data
notes | Day of Jan 2016 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | day | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
Hydrolysis slurry thick. | 1 | 2503.2 | 64.4 | 270 | 1 | 1253.2 | 9535 | 1 | 5.14 | 7.08 | 1 |  |  | 1 | [6 empty] | 1 | 9 | 0 | 534957 | 4953
Hydrolysis slurry thinning out. | 2 | 1772.2 | 60.8 | 376 | 2 | 616.3 | 5028.5 | 2 | 4.9 | 6.96 | 2 |  |  | 2 | [6 empty] | 2 | 7 | 1 | 536757 | 4968
| 3 | 2538.5 | 64.2 | 274 | 3 | 600.5 | 7611.3 | 3 | 4.76 | 7.04 | 3 |  |  | 3 | [6 empty] | 3 | 4 | 8 | 539257 | 4998
Pump blocked & top box overflowing. Separator pipe plugged. Flare water trap frozen & heat tape cold. Later manaully emptied water trap & started flare. | 4 | 1916.1 | 63.7 | 269 | 4 | 626.3 | 7354.1 | 4 | 4.89 | 7.19 | 4 |  |  | 4 | [6 empty] | 4 | 4 | 0 | 541257 | 5009
| 5 | 2224.3 | 65.1 | 283 | 5 | 647.8 | 7842.6 | 5 |  |  | 5 |  |  | 5 | [6 empty] | 5 | 4 | 0 | 543857 | 5033
| 6 | 2104.8 | 63.9 | 315 | 6 | 583.2 | 7197.6 | 6 | 4.9 | 7.07 | 6 |  |  | 6 | [6 empty] | 6 | 4 | 4 | 545657 | 5050
| 7 | 2428.4 | 66.1 | 205 | 7 | 593.6 | 8223.7 | 7 |  |  | 7 |  |  | 7 | [6 empty] | 7 | 3 | 1 | 548157 | 5073
| 8 | 2362.9 | 67.2 | 254 | 8 | 620.5 | 7704.4 | 8 | 5.16 | 7.17 | 8 |  |  | 8 | [6 empty] | 8 | 3 | 2 | 550357 | 5092
| 9 | 2184 | 66.8 | 259 | 9 | 580.4 | 7449.8 | 9 | 5.42 | 7.17 | 9 |  |  | 9 | [6 empty] | 9 | 4 | 0 | 552557 | 5113
Lots of wood chips in digestate | 10 | 1974.9 | 65.6 | 360 | 10 | 569.1 | 6952.2 | 10 | 5.38 | 7.05 | 10 |  |  | 10 | [6 empty] | 10 | 5 | 0 | 554657 | 5133
| 11 | 1935.5 | 66.2 | 348 | 11 | 557.3 | 6834.7 | 11 | 5.78 | 7.18 | 11 |  |  | 11 | [6 empty] | 11 | 6 | 0 | 557057 | 5156
data taken at 2 pm vs. 8 am | 12 | 1808.9 | 63 | 170 | 12 | 543.8 | 605.1 | 12 | 5.42 | 7.17 | 12 |  |  | 12 | [6 empty] | 12 | 5 | 0 | 558457 | 5169
| 13 | 1541.7 | 65.5 | 274 | 13 | 612.2 | 5395.9 | 13 | 5.4 | 7.35 | 13 |  |  | 13 | [6 empty] | 13 | 6 | 0 | 560057 | 5184
| 14 | 1607.3 | 64.8 | 285 | 14 | 572.2 | 5246.7 | 14 | 5.42 | 7.26 | 14 |  |  | 14 | [6 empty] | 14 | 7 | 0 | 561757 | 5200
| 15 | 1489.9 | 65.4 | 253 | 15 | 584.1 | 4905.1 | 15 | 5.53 | 7.15 | 15 |  |  | 15 | [6 empty] | 15 | 7 | 0 | 563157 | 5213
| 16 | 1259.2 | 63.9 | 268 | 16 | 613.8 | 4793.9 | 16 | 5.49 | 7.17 | 16 |  |  | 16 | [6 empty] | 16 | 7 | 0 | 564457 | 5226
| 17 | 1078.2 | 64.8 | 243 | 17 | 633.6 | 4042.1 | 17 | 5.88 | 7.38 | 17 |  |  | 17 | [6 empty] | 17 | 7 | 0 | 565457 | 5238
| 18 | 1091.1 | 64.4 | 241 | 18 | 547.4 | 3828.9 | 18 |  |  | 18 |  |  | 18 | [6 empty] | 18 | 8 | 0 | 566657 | 5250
| 19 | 984.4 | 62.8 | 260 | 19 | 590.4 | 3834.6 | 19 | 5.57 | 7.45 | 19 |  |  | 19 | [6 empty] | 19 | 7 | 0 | 567657 | 5260
Thin digestate | 20 | 832.2 | 63.9 | 213 | 20 | 602 | 3128.8 | 20 | 5.49 | 7.24 | 20 |  |  | 20 | [6 empty] | 20 | 6 | 0 | 568557 | 5270
Thinnish digestate | 21 | 877.3 | 62.6 | 276 | 21 | 594.4 | 3312 | 21 | 5.56 | 7.28 | 21 |  |  | 21 | [6 empty] | 21 | 7 | 0 | 569357 | 5279
| 22 | 724.2 | 61.8 | 240 | 22 | 610.4 | 2795.5 | 22 | 5.69 | 7.3 | 22 |  |  | 22 | [6 empty] | 22 | 6 | 4 | 570057 | 5287
| 23 | 1074 | 61.3 | 235 | 23 | 618 | 3248 | 23 | 5.22 | 7.15 | 23 |  |  | 23 | [6 empty] | 23 | 6 | 0 | 571157 | 5296
| 24 | 837 | 62.1 | 331 | 24 | 616 | 3090 | 24 | 5.11 | 7.15 | 24 |  |  | 24 | [6 empty] | 24 | 7 | 0 | 572057 | 5305
| 25 | 725.2 | 61.6 | 323 | 25 | 563.4 | 2826.5 | 25 | 5.29 | 7.26 | 25 |  |  | 25 | [6 empty] | 25 | 6 | 0 | 572757 | 5313
| 26 | 1168.7 | 60.7 | 176 | 26 | 581.8 | 3218.8 | 26 | 5.16 | 7.26 | 26 |  |  | 26 | [6 empty] | 26 | 6 | 0 | 573957 | 5322
| 27 | 1532 | 59.6 | 211 | 27 | 566.9 | 3501.5 | 27 | 5 | 7.28 | 27 |  |  | 27 | [6 empty] | 27 | 8 | 0 | 575457 | 5332
| 28 | 1204.8 | 61 | 233 | 28 | 553 | 4100.2 | 28 | 5.05 | 7.3 | 28 |  |  | 28 | [6 empty] | 28 | 8 | 0 | 576757 | 5345
| 29 | 1002.7 | 61.9 | 213 | 29 | 670.2 | 3777 | 29 | 5.04 | 7.32 | 29 |  |  | 29 | [6 empty] | 29 | 6 | 16 | 577157 | 5355
| 30 | 1883.9 | 60.7 | 120 | 30 | 521 | 4921 | 30 | 4.95 | 7.28 | 30 |  |  | 30 | [6 empty] | 30 | 8 | 0 | 579657 | 5370
| 31 | 1860.1 | 60.1 | 201 | 31 | 602.8 | 5190.2 | 31 | 4.93 | 7.27 | 31 | [9 empty] | 31 | 7 | 0 | 581557 | 5384
| average | 1565.4065 | 63.4161 | 257.3871 | average | 614.3742 | 5080.5065 |  | 5.2689 | 7.2096 |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | average
| SD | 569.6902 | 2.1008 | 56.4628 | SD | 122.855 | 2083.0348 |  | 0.29713 | 0.11257 |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SD

## Feb'16
VTCAD February 2016 Operational Data
notes | Day of Feb 2016 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | day | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 1594 | 61.7 | 148 | 1 | 514.2 | 5590.8 | 1 | 5.15 | 7.3 | 1 |  |  | 1 | [6 empty] | 1 | 8 | 0 | 583257 | 5401
| 2 | 2004.2 | 59.2 | 86 | 2 | 559.3 | 5372.1 | 2 |  |  | 2 |  |  | 2 | [6 empty] | 2 | 8 | 0 | 585457 | 5426
| 3 | 1679 | 60.8 | 115 | 3 | 595.2 | 5838.7 | 3 |  |  | 3 |  |  | 3 | [6 empty] | 3 | 7 | 0 | 597257 | 5434
| 4 | 1485.2 | 62.2 | 136 | 4 | 570.4 | 5666.4 | 4 |  |  | 4 |  |  | 4 | [6 empty] | 4 | 6 | 0 | 588557 | 5448
| 5 | 1577.6 | 63.1 | 267 | 5 | 595.1 | 5852.7 | 5 | 5.28 | 7.39 | 5 |  |  | 5 | [6 empty] | 5 | 7 | 0
| 6 | 1953.4 | 64.8 | 253 | 6 | 611.5 | 6525.9 | 6 | 5.47 | 7.42 | 6 |  |  | 6 | [6 empty] | 6 | 6 | 0 | 592157 | 5483
| 7 | 1621.8 | 63.2 | 358 | 7 | 603.6 | 6160.3 | 7 | 5.3 | 7.29 | 7 |  |  | 7 | [6 empty] | 7 | 6 | 0 | 593757 | 5500
| 8 | 1747.3 | 64 | 311 | 8 | 563.7 | 6431 | 8 | 5.49 | 7.3 | 8 |  |  | 8 | [6 empty] | 8 | 6 | 0 | 595657 | 5518
| 9 | 2042.1 | 64.6 | 197 | 9 | 579 | 6689.7 | 9 | 5.18 | 7.25 | 9 |  |  | 9 | [6 empty] | 9 | 5 | 0 | 597457 | 5535
| 10 | 1833.6 | 64.6 | 327 | 10 | 661 | 6743.4 | 10 | 5.17 | 7.2 | 10 |  |  | 10 | [6 empty] | 10 | 6 | 0 | 599357 | 5553
| 11 | 1696.5 | 65.2 | 257 | 11 | 626.1 | 6250.4 | 11 | 5.06 | 7.24 | 11 |  |  | 11 | [6 empty] | 11 | 7 | 0 | 601257 | 5573
| 12 | 1916.6 | 64.6 | 360 | 12 | 554.8 | 6200.9 | 12 | 5.11 | 7.24 | 12 |  |  | 12 | [6 empty] | 12 | 5 | 0 | 602957 | 5589
| 13 | 1903.6 | 64.4 | 227 | 13 | 580.4 | 6542.2 | 13 | 5.03 | 7.18 | 13 |  |  | 13 | [6 empty] | 13 | 5 | 0 | 604757 | 5606
| 14 | 1820.2 | 64.8 | 367 | 14 | 496.8 | 5526.9 | 14 | 5.02 | 7.15 | 14 |  |  | 14 | [6 empty] | 14 | 7 | 0 | 606657 | 5621
| 15 | 1714.7 | 64.4 | 393 | 15 | 584.6 | 5500.5 | 15 | 5.11 | 7.24 | 15 |  |  | 15 | [6 empty] | 15 | 7 | 0 | 608457 | 5638
| 16 | 1741.4 | 64 | 229 | 16 | 570.2 | 5859.8 | 16 |  |  | 16 |  |  | 16 | [6 empty] | 16 | 7 | 2 | 610257 | 5655
| 17 | 2367.3 | 61.9 | 202 | 17 | 606.5 | 6056.7 | 17 | 5.05 | 7.37 | 17 |  |  | 17 | [6 empty] | 17 | 6 | 0 | 612457 | 5670
| 18 | 2089.8 | 62.1 | 745 | 18 | 594.2 | 6098.5 | 18 |  |  | 18 |  |  | 18 | [6 empty] | 18 | 6 | 0 | 614657 | 5587
| 19 | 1632 | 63.5 | 176 | 19 | 559.1 | 5649.9 | 19 | 5.07 | 7.22 | 19 |  |  | 19 | [6 empty] | 19 | 6 | 0 | 616357 | 5704
| 20 | 2451 | 63.2 | 82 | 20 | 521 | 5988 | 20 | 4.96 | 7.2 | 20 |  |  | 20 | [6 empty] | 20 | 7 | 0 | 618857 | 5721
genset tripped | 21 | 950 | 65.9 | 127 | 21 | 578 | 2176 | 21 | 5.13 | 7.3 | 21 |  |  | 21 | [6 empty] | 21 | 3 | 47 | 619857 | 5727
| 22 | 605.1 | 65.9 | 110 | 22 | 505.6 | 1928.2 | 22 | 5.09 | 7.21 | 22 |  |  | 22 | [6 empty] | 22 | 1 | 52 | 620357 | 5732
| 23 | 2433.2 | 61.2 | 164 | 23 | 471.7 | 6066.5 | 23 | 4.96 | 7.2 | 23 |  |  | 23 | [6 empty] | 23 | 7 | 0 | 623057 | 5751
| 24 | 2601.3 | 61.6 | 105 | 24 | 556.5 | 5963.2 | 24 | 5.17 | 7.15 | 24 |  |  | 24 | [6 empty] | 24 | 6 | 0 | 625957 | 5769
| 25 | 2751.3 | 63 | 120 | 25 | 534.5 | 5796 | 25 | 5.08 | 7.24 | 25 |  |  | 25 | [6 empty] | 25 | 6 | 0 | 628677 | 5785
genset tripped | 26 | 2508.9 | 63.3 | 142 | 26 | 561.1 | 3311.6 | 26 | 5.24 | 7.43 | 26 |  |  | 26 | [6 empty] | 26 | 7 | 8 | 631057 | 5800
| 27 | 2594.6 | 63.3 | 218 | 27 | 558.7 | 6384.2 | 27 | 5.23 | 7.18 | 27 |  |  | 27 | [6 empty] | 27 | 6 | 0 | 633657 | 5817
oil change | 28 | 2895.8 | 62.6 | 103 | 28 | 597.5 | 6616.3 | 28 | 5.17 | 7.17 | 28 |  |  | 28 | [6 empty] | 28 | 6 | 1 | 636657 | 5836
| 29 | 2419.6 | 64.2 | 100 | 29 | 505.8 | 6737.5 | 29 | 5.17 | 7.18 | 29 |  |  | 29 | [6 empty] | 29 | 5 | 1 | 638957 | 5875
| average | 1952.7966 | 63.3552 | 221.5517 | average | 566.0724 | 5707.7345 |  | 5.1537 | 7.2521 |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | average
| SD | 514.3989 | 1.5702 | 138.1776 | SD | 41.9166 | 1200.2131 |  | 0.13419 | 0.082303 |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SD

## Mar'16
VTCAD March 2016 Operational Data
notes | Day of March 2016 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | H2S (ppm) 24 h | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 2552.2 | 64.3 | 306 |  | 1 | 551.5 | 6215.5 | 1 | 5.01 | 7.1 | 1 |  |  | 1 | [6 empty] | 7 | 3 | 641857 | 5873
| 2 | 2875.6 | 64.5 | 230 |  | 2 | 528 | 6634.9 | 2 |  |  | 2 |  |  | 2 | [6 empty] | 5 | 0 | 644457 | 5890
oil change | 3 | 2523.1 | 65.8 | 458 |  | 3 | 566.6 | 6348.5 | 3 | 5.02 | 7.12 | 3 |  |  | 3 | [6 empty] | 6 | 1 | 646957 | 5907
8:00 | 4 | 2421.6 | 64.2 | 465 |  | 4 | 621.1 | 6472.2 | 4 | 5.16 | 7.18 | 4 |  |  | 4 | [6 empty] | 6 | 1 | 679457 | 5926
hyd @ 61% | 5 | 2237 | 65.5 | 394 |  | 5 | 580 | 6162 | 5 | 5.09 | 7.11 | 5 |  |  | 5 | [6 empty] | 6 | 0 | 651757 | 5943
| 6 | 2159 | 63.7 | 447 |  | 6 | 606.7 | 6511.7 | 6 | 5.11 | 7.08 | 6 |  |  | 6 | [6 empty] | 6 | 0 | 654057 | 5962
| 7 | 2793.6 | 60.7 | 357 |  | 7 | 609.2 | 6546.8 | 7 | 5.08 | 7.11 | 7 |  |  | 7 | [6 empty] | 8 | 1 | 657657 | 5986
| 8 | 2957.1 | 61.4 | 283 |  | 8 | 513.3 | 6122.1 | 8 | 5.02 | 7.05 | 8 |  |  | 8 | [6 empty] | 5 | 1 | 660057 | 5999
| 9 | 2448 | 63.2 | 391 |  | 9 | 506.8 | 5489.9 | 9 | 5.12 | 7.06 | 9 |  |  | 9 | [6 empty] | 7 | 4 | 662257 | 6013
| 10 | 2659.1 | 62.7 | 282 |  | 10 | 578.8 | 5705 | 10 | 5.07 | 7.07 | 10 |  |  | 10 | [6 empty] | 8 | 0 | 665157 | 6030
| 11 | 2563.8 | 61.9 | 273 |  | 11 | 661.6 | 5665 | 11 | 5.21 | 7.1 | 11 |  |  | 11 | [6 empty] | 7 | 1 | 667657 | 6046
| 12 | 1852.6 | 65.2 | 16 |  | 12 | 569.9 | 5388.3 | 12 | 5.18 | 6.98 | 12 |  |  | 12 | [6 empty] | 6 | 0 | 669557 | 6061
| 13 | 2224.3 | 63.8 | 318 | 303 | 13 | 553.9 | 5344.3 | 13 | 5.3 | 7.02 | 13 |  |  | 13 | [6 empty] | 8 | 0 | 671857 | 6077
| 14 | 2182.3 | 62.1 | 161 | 69 | 14 | 545.9 | 5198.5 | 14 | 5.28 | 7.01 | 14 |  |  | 14 | [6 empty] | 7 | 0 | 673857 | 6090
| 15 | 2180.1 | 65.6 | 431 | 424 | 15 | 563.8 | 4779.9 | 15 | 5.29 | 7.15 | 15 |  |  | 15 | [6 empty] | 9 | 0 | 679257 | 6105
genset down; cracked manifold | 16 |  |  |  |  | 16 |  |  | 16 |  |  | 16 |  |  | 16
| 17 |  |  |  |  | 17 |  |  | 17 | 5.16 | 7.08 | 17 |  |  | 17
genset down; cracked manifold | 18 | 1300 | 65.2 | 384 |  | 18 | 1706 | 2684 | 18 | 5.21 | 7.04 | 18 |  |  | 18 | [6 empty] | 4 | 138
| 19 | 1680 | 62.6 | 375 | 410 | 19 | 609 | 3624 | 19 | 5.19 | 7.04 | 19 |  |  | 19 | [6 empty] | 6 | 51 | 679357 | 6127
| 20 | 1399 | 61.9 | 367 | 397 | 20 | 629 | 2984 | 20 | 5.21 | 7.01 | 20 |  |  | 20 | [6 empty] | 2 | 34 | 680857 | 6139
| 21 | 2549 | 59.6 | 357 | 367 | 21 | 536 | 5412 | 21 | 5.33 | 6.93 | 21 |  |  | 21 | [6 empty] | 3 | 0 | 683357 | 6159
| 22 | 2382 | 59 | 490 | 484 | 22 | 600 | 5355 | 22 | 5.15 | 6.88 | 22 |  |  | 22 | [6 empty] | 4 | 2 | 685757 | 6180
2G screen frozen | 23 | 2419.6 | 59.4 | 511 | 497 | 23 | 548.1 | 5302.7 | 23 | 5.09 | 6.85 | 23 |  |  | 23 | [6 empty] | 4 | 2
| 24 | 2384.8 | 60.6 | 551 | 528 | 24 | 575.2 | 5162.5 | 24 | 5.11 | 6.83 | 24 |  |  | 24 | [6 empty] | 3 | 4 | 690557 | 6219
hyrolysate is oily | 25 | 2742.7 | 61.5 | 609 | 605 | 25 | 641.3 | 6049.9 | 25 | 5.15 | 6.78 | 25 |  |  | 25 | [6 empty] | 1 | 0 | 693457 | 6243
| 26 | 2723.2 | 64.7 | 509 | 577 | 26 | 641.1 | 6201.1 | 26 | 5.04 | 6.72 | 26 |  |  | 26 | [6 empty] | 1 | 0 | 696057 | 6265
| 27 | 2781.9 | 63.3 | 456 | 575 | 27 | 549.5 | 7461.9 | 27 | 5.19 | 6.72 | 27 |  |  | 27 | [6 empty] | 0 | 2 | 699057 | 6290
digestate tinted green | 28 | 2905 | 64.9 | 447 | 501 | 28 | 493 | 8355 | 28 | 5.13 | 6.82 | 28 |  |  | 28 | [6 empty] | 0 | 9 | 702057 | 6314
pump 7 out | 29 | 2825.1 | 67.8 | 296 | 389 | 29 | 537 | 9017.7 | 29 | 5.12 | 6.97 | 29 |  |  | 29 | [6 empty] | 0 | 18 | 704657 | 6336
| 30 | 3079.4 | 65.5 | 393 | 337 | 30 | 582.6 | 8444.5 | 30 | 5.09 | 6.94 | 30 |  |  | 30 | [6 empty] | 0 | 7 | 707957 | 6361
| average | 2421.4679 | 63.2357 | 377.0357 |  | average | 614.4607 | 5879.9607 |  | 5.1468 | 6.9911 |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| SD | 444.8533 | 2.2049 | 123.1607 |  | SD | 218.1331 | 1425.7186 |  | 0.085896 | 0.1294 |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Apr'16
VTCAD April 2016 Operational Data
notes | Day of Apr 2016 | biogas consumed (m3/day) | current CH4 (%) | 24 hr avg CH4 (%) | current H2S (ppm) | 24 hr avg H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 | 2327 | 64.5 |  | 598 | 564 | 1 | 434.5 | 7278.7 | 1 | 4.93 | 6.85 | 1 |  |  | 1 | [6 empty] | 0 | 28 | 712357 | 6398
| 2 | 3427 | 66.5 |  | 323 | 434 | 2 | 592.3 | 8880.9 | 2 | 5.09 | 6.74 | 2 |  |  | 2 | [6 empty] | 0 | 4 | 716157 | 6424
| 3 | 2461.7 | 66.6 | 66.5 | 314 | 354 | 3 | 529.1 | 8962.3 | 3 | 5.28 | 6.83 | 3 |  |  | 3 | [6 empty] | 0 | 101 | 718357 | 6446
| 4 | 3185.5 | 67.5 | 66.7 | 328 | 299 | 4 | 670.8 | 9170.3 | 4 | 5.17 | 6.95 | 4 |  |  | 4 | [6 empty] | 1 | 152 | 721157 | 6467
| 5 | 2476.9 | 67 | 67 | 428 | 404 | 5 | 543.2 | 6918.1 | 5 | 5.11 | 7.01 | 5 |  |  | 5 | [6 empty] | 4 | 145 | 724457 | 6492
sllightly green digestate | 6 | 3134.4 | 65.8 | 66.2 | 460 | 450 | 6 | 567.6 | 8822.4 | 6 | 5.31 | 7.01 | 6 |  |  | 6 | [6 empty] | 0 | 60 | 727057 | 6511
greenish digestate | 7 | 2725.1 | 67 | 65.2 | 467 | 481 | 7 | 589.4 | 7844.1 | 7 | 5.19 | 7.04 | 7 |  |  | 7 | [6 empty] | 2 | 80 | 729757 | 6532
| 8 | 2197.4 | 65 |  | 372 |  | 8 | 578.9 | 7665.6 | 8 | 5.04 | 7.19 | 8 |  |  | 8 | [6 empty] | 2 | 59 | 732057 | 6554
| 9 | 3050.9 | 65.6 | 65 | 378 | 400 | 9 | 530.1 | 8318.2 | 9 | 4.85 | 7 | 9 |  |  | 9 | [6 empty] | 1 | 12 | 735057 | 6576
| 10 | 2754.6 | 66.2 | 65.5 | 345 | 379 | 10 | 552.5 | 8903.5 | 10 | 5 | 6.98 | 10 |  |  | 10 | [6 empty] | 0 | 18 | 737857 | 6601
| 11 | 2659.2 | 64.5 | 64.8 | 336 | 348 | 11 | 537.7 | 8463.8 | 11 | 4.99 | 7.01 | 11 |  |  | 11 | [6 empty] | 0 | 10 | 740557 | 6624
see log book for pH info | 12 | 3400.6 | 65.9 | 62.9 | 371 | 390 | 12 | 625.4 | 8610.3 | 12 | 5.05 | 6.93 | 12 |  |  | 12 | [6 empty] | 0 | 9 | 744057 | 6649
| 13 | 2581 | 66.1 | 65.6 | 369 | 372 | 13 | 577 | 8120 | 13 | 5.09 | 6.91 | 13 |  |  | 13 | [6 empty] | 2 | 28 | 746657 | 6671
| 14 | 3013.8 | 66.4 | 65.7 | 378 | 385 | 14 | 567.8 | 8903.5 | 14 | 5.11 | 6.95 | 14 |  |  | 14 | [6 empty] | 0 | 18 | 749657 | 6695
| 15 | 2931.2 | 66.8 | 65.7 | 386 | 440 | 15 | 634.5 | 8934.7 | 15 | 5.09 | 6.99 | 15 |  |  | 15 | [6 empty] | 0 | 27 | 752657 | 6719
| 16 | 3022 | 67.4 | 61.3 | 414 | 490 | 16 | 553.5 | 8514.6 | 16 | 5.01 | 6.95 | 16 |  |  | 16 | [6 empty] | 0 | 14 | 755757 | 6743
| 17 | 2609.6 | 62 | 63.9 | 489 | 615 | 17 | 540.7 | 8786.8 | 17 | 5.13 | 6.97 | 17 |  |  | 17 | [6 empty] | 0 | 10 | 758357 | 6767
| 18 | 2257 | 65.5 | 62.1 | 477 | 632 | 18 | 501 | 6467 | 18 | 5.17 | 7.05 | 18 |  |  | 18 | [6 empty] | 1 | 3 | 760657 | 6786
| 19 | 2523.5 | 64 | 62.6 | 441 | 584 | 19 | 548.1 | 7210.1 | 19 | 5.16 | 7.08 | 19 |  |  | 19 | [6 empty] | 1 | 16 | 763257 | 6808
| 20 | 2856.7 | 63.8 | 62.7 | 440 | 467 | 20 | 540.8 | 7563.5 | 20 | 5.02 | 7.06 | 20 |  |  | 20 | [6 empty] | 0 | 0 | 766057 | 6832
| 21 | 2746.6 | 64.8 | 62.8 | 446 | 464 | 21 | 560 | 8116.5 | 21 | 5.08 | 6.98 | 21 |  |  | 21 | [6 empty] | 0 | 2 | 768857 | 6853
| 22 | 2688.4 | 65.4 | 63.7 | 538 | 624 | 22 | 570.9 | 8304.2 | 22 | 5.14 | 6.99 | 22 |  |  | 22 | [6 empty] | 1 | 12 | 771657 | 6879
| 23 | 1833.2 | 66 | 65 | 434 | 599 | 23 | 580.6 | 6071.1 | 23 | 5.11 | 6.99 | 23 |  |  | 23 | [6 empty] | 1 | 83 | 773557 | 6898
| 24 | 2376 | 64.7 | 64 | 432 | 460 | 24 | 540 | 8751.3 | 24 | 5.17 | 6.98 | 24 |  |  | 24 | [6 empty] | 0 | 7 | 775857 | 6920
| 25 | 2036.8 | 66.6 | 64.4 | 370 | 411 | 25 | 541.4 | 6551.7 | 25 |  | 7.06 | 25 |  |  | 25 | [6 empty] | 2 | 58 | 777957 | 6938
water trap | 26 | 2323.2 | 65.8 | 64.2 | 392 | 438 | 26 | 560.6 | 7509.1 | 26 | 5.3 | 7.08 | 26 |  |  | 26 | [6 empty] | 1 | 28 | 780357 | 6960
| 27 | 2773.2 | 65.9 | 64.9 | 500 | 493 | 27 | 585.7 | 8201.2 | 27 | 5.29 | 7.06 | 27 |  |  | 27 | [6 empty] | 2 | 10 | 783057 | 6982
| 28 | 2914.3 | 66.2 | 63.8 | 518 | 571 | 28 | 600.5 | 7865.1 | 28 | 5.21 | 7.09 | 28 |  |  | 28 | [6 empty] | 0 | 0 | 785957 | 7006
| 29 | 2835.1 | 64.9 | 64.2 | 547 | 620 | 29 | 572.9 | 8223.3 | 29 | 5.11 | 7.14 | 29 |  |  | 29 | [6 empty] | 0 | 7 | 788857 | 7030
9:10 | 30 | 2787.8 | 65 | 63.2 | 461 | 554 | 30 | 533.8 | 7758.7 | 30 | 5.19 | 7.27 | 30 |  |  | 30 | [6 empty] | 0 | 5 | 791857 | 7056
| average | 2696.99 | 65.6467 | 64.4296 | 425.0667 | 473.1724 | average | 562.0433 | 8056.3533 |  | 5.1169 | 7.0047 |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| SD | 376.8193 | 1.1872 | 1.4689 | 71.7976 | 95.5372 | SD | 42.3186 | 822.8226 |  | 0.10833 | 0.10271 |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Sheet2 (hidden)
VTCAD ___MONTH___ 2015 Operational Data
notes | Day of _____ 2015 | biogas consumed (m3/day) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
| 1 |  |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
| 2 |  |  |  | 2 |  |  | 2 |  |  | 2 |  |  | 2
| 3 |  |  |  | 3 |  |  | 3 |  |  | 3 |  |  | 3
| 4 |  |  |  | 4 |  |  | 4 |  |  | 4 |  |  | 4
| 5 |  |  |  | 5 |  |  | 5 |  |  | 5 |  |  | 5
| 6 |  |  |  | 6 |  |  | 6 |  |  | 6 |  |  | 6
| 7 |  |  |  | 7 |  |  | 7 |  |  | 7 |  |  | 7
| 8 |  |  |  | 8 |  |  | 8 |  |  | 8 |  |  | 8
| 9 |  |  |  | 9 |  |  | 9 |  |  | 9 |  |  | 9
| 10 |  |  |  | 10 |  |  | 10 |  |  | 10 |  |  | 10
| 11 |  |  |  | 11 |  |  | 11 |  |  | 11 |  |  | 11
| 12 |  |  |  | 12 |  |  | 12 |  |  | 12 |  |  | 12
| 13 |  |  |  | 13 |  |  | 13 |  |  | 13 |  |  | 13
| 14 |  |  |  | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 15 |  |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15
| 16 |  |  |  | 16 |  |  | 16 |  |  | 16 |  |  | 16
| 17 |  |  |  | 17 |  |  | 17 |  |  | 17 |  |  | 17
| 18 |  |  |  | 18 |  |  | 18 |  |  | 18 |  |  | 18
| 19 |  |  |  | 19 |  |  | 19 |  |  | 19 |  |  | 19
| 20 |  |  |  | 20 |  |  | 20 |  |  | 20 |  |  | 20
| 21 |  |  |  | 21 |  |  | 21 |  |  | 21 |  |  | 21
| 22 |  |  |  | 22 |  |  | 22 |  |  | 22 |  |  | 22
| 23 |  |  |  | 23 |  |  | 23 |  |  | 23 |  |  | 23
| 24 |  |  |  | 24 |  |  | 24 |  |  | 24 |  |  | 24
| 25 |  |  |  | 25 |  |  | 25 |  |  | 25 |  |  | 25
| 26 |  |  |  | 26 |  |  | 26 |  |  | 26 |  |  | 26
| 27 |  |  |  | 27 |  |  | 27 |  |  | 27 |  |  | 27
| 28 |  |  |  | 28 |  |  | 28 |  |  | 28 |  |  | 28
| 29 |  |  |  | 29 |  |  | 29 |  |  | 29 |  |  | 29
| 30 |  |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30
| average | #DIV/0! | #DIV/0! | #DIV/0! | average | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| SD | #DIV/0! | #DIV/0! | #DIV/0! | SD | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## May'16
VTCAD May 2016 Operational Data
notes | Day of May 2016 | biogas consumed (m3/day) | CH4 (%) | CH4 (%) 24 hr avg | H2S (ppm) | H2S (ppm) 24 hr avg | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
8:15 | 1 | 2798 | 64 | 63.9 | 429 | 496 | 1 | 502 | 6868 | 1 | 5.15 | 7.07 | 1 |  |  | 1 | [6 empty] | 0 | 0 | 794657 | 7078
| 2 | 2740.9 | 64.1 | 63.2 | 398 | 428 | 2 | 524.1 | 6821.9 | 2 | 5.28 | 7.11 | 2 |  |  | 2 | [6 empty] | 0 | 0 | 797657 | 7104
| 3 | 2817.4 | 61.9 | 61.6 | 399 | 423 | 3 | 605.1 | 6560.3 | 3 | 5.27 | 7.05 | 3 |  |  | 3 | [6 empty] | 0 | 0 | 800257 | 7126
500 hr oil change | 4 | 2889.9 | 60.1 | 59.6 | 396 | 416 | 4 | 596.5 | 6447.4 | 4 | 5.2 | 7.04 | 4 |  |  | 4 | [6 empty] | 0 | 0 | 803257 | 7151
0' large bubbles | 5 | 2920.4 | 60 | 58.8 | 396 | 410 | 5 | 608.6 | 6350.6 | 5 | 5.06 | 7.08 | 5 |  |  | 5 | [6 empty] | 0 | 0 | 806057 | 7173
0' | 6 | 2673 | 64.1 | 60.7 | 422 | 440 | 6 | 699 | 5894 | 6 | 5.08 | 7.07 | 6 |  |  | 6 | [6 empty] | 0 | 0 | 808757 | 7197
1/2' foam digester box | 7 | 2775.2 | 62.3 | 61.4 | 450 | 5863 | 7 | 548.6 | 6184.2 | 7 | 5.07 | 6.98 | 7 |  |  | 7 | [6 empty] | 0 | 0 | 811657 | 7222
1/2' box | 8 | 2719.4 | 64.7 | 62.1 | 400 | 456 | 8 | 546.5 | 6195.2 | 8 | 5.1 | 7.02 | 8 |  |  | 8 | [6 empty] | 0 | 0 | 814357 | 7246
0' | 9 | 2769.3 | 69.9 | 64.5 | 401 | 407 | 9 | 524.1 | 6642.6 | 9 | 5.32 | 7.14 | 9 |  |  | 9 | [6 empty] | 0 | 0 | 817257 | 7270
0' large bubbles | 10 | 2874.1 | 65.7 | 3 | 664 | 630 | 10 | 571.9 | 7355.1 | 10 | 5.24 | 7.07 | 10 |  |  | 10 | [6 empty] | 0 | 0 | 820157 | 7295
1/2 foot / hydrolyzer extra bubbly | 11 | 3100.9 | 60.9 | 62.2 | 736 | 888 | 11 | 662.7 | 7750.2 | 11 | 5.13 | 7.04 | 11 |  |  | 11 | [6 empty] | 0 | 0 | 823257 | 7318
| 12 | 2999 | 65.6 | 62.5 | 699 | 672 | 12 | 579.8 | 7300.8 | 12 | 5 | 7.01 | 12 |  |  | 12 | [6 empty] | 0 | 0 | 826357 | 7343
0' | 13 | 2588 | 65 | 63.9 | 819 | 1103 | 13 | 565 | 7793 | 13 | 5.05 | 7.09 | 13 |  |  | 13 | [6 empty] | 1 | 16 | 828957 | 7366
7:40 1/2 foot of big bubbles | 14 | 3383 | 68.1 | 69.2 | 745 | 920 | 14 | 546.9 | 7539.7 | 14 | 5.18 | 7.08 | 14 |  |  | 14 | [6 empty] | 0 | 5 | 832457 | 7390
Foam <1/2" | 15 | 2905 | 66.9 | 67.6 | 602 | 840 | 15 | 499 | 7214 | 15 | 5.23 | 7.11 | 15 |  |  | 15 | [6 empty] | 0 | 0 | 835257 | 7413
Foam <1/2" | 16 | 2823.2 | 65.9 | 65.4 | 568 | 606 | 16 | 550.5 | 6890.4 | 16 | 5.29 | 7.11 | 16 |  |  | 16 | [6 empty] | 0 | 0 | 838157 | 7437
Foam <1/2" | 17 | 2862.9 | 65.6 | 64.5 | 649 | 649 | 17 | 576.8 | 7146.6 | 17 | 5.22 | 6.98 | 17 |  |  | 17 | [6 empty] | 0 | 1 | 841057 | 7460
Foam <1/2" | 18 | 2920.3 | 64.2 | 63.2 | 677 | 753 | 18 | 638.4 | 6926.4 | 18 | 5.19 | 6.97 | 18 |  |  | 18 | [6 empty] | 0 | 1 | 844157 | 7485
Foam <1/2" | 19 | 2757.4 | 66.3 | 64.2 | 655 | 784 | 19 | 548 | 7074.3 | 19 | 5.01 | 6.97 | 19 |  |  | 19 | [6 empty] | 0 | 0 | 846857 | 7509
Foam <1/2" | 20 | 2484.2 | 66.6 | 66.2 | 631 | 756 | 20 | 593.2 | 6964.8 | 20 | 5.11 | 7.02 | 20 |  |  | 20 | [6 empty] | 1 | 53 | 849457 | 7529
Foam <1/2" | 21 | 2987.2 | 66.8 | 66 | 752 | 934 | 21 | 635.2 | 8898.4 | 21 | 4.89 | 6.95 | 21 |  |  | 21 | [6 empty] | 0 | 37 | 852457 | 7553
Foam <1/2"; oily sheen in hydrolyzer | 22 | 2883 | 67.5 | 66.5 | 717 | 972 | 22 | 491 | 8715 | 22 | 5.1 | 7.03 | 22 |  |  | 22 | [6 empty] | 0 | 61 | 855357 | 7576
Foam <1/2" | 23 | 3118 | 67.2 | 67.1 | 676 | 806 | 23 | 530 | 8811.4 | 23 | 5.09 | 6.98 | 23 |  |  | 23 | [6 empty] | 0 | 26 | 858557 | 7601
Foam <1/2" | 24 | 2460.3 | 69.9 | 66.4 | 769 | 978 | 24 | 554.9 | 7140.8 | 24 | 5.08 | 6.98 | 24 |  |  | 24 | [6 empty] | 1 | 52 | 860957 | 7620
Foam <1/2" | 25 | 2745 | 65.5 | 65 | 740 | 914 | 25 | 606 | 6677 | 25 | 5.02 | 6.98 | 25 |  |  | 25 | [6 empty] | 0 | 0 | 863757 | 7644
Foam <1/2" | 26 | 2868 | 65.8 | 62.1 | 517 | 813 | 26 | 611 | 6891 | 26 | 5.06 | 7.03 | 26 |  |  | 26 | [6 empty] | 0 | 0 | 866657 | 7668
Foam <1/2" | 27 | 3004.1 | 65.6 | 64.9 | 728 | 815 | 27 | 586.8 | 7299.1 | 27 | 5.07 | 6.99 | 27 |  |  | 27 | [6 empty] | 0 | 0 | 870057 | 7698
Foam <1/2" | 28 | 3051.1 | 65.8 | 63.9 | 981 | 1010 | 28 | 488 | 7560 | 28 | 4.99 | 7.01 | 28 |  |  | 28 | [6 empty] | 0 | 7 | 872957 | 7718
Foam 1/2" | 29 | 2922.5 | 66.2 | 64.9 | 881 | 1138 | 29 | 506.3 | 7147.3 | 29 | 5.85 | 7 | 29 |  |  | 29 | [6 empty] | 0 | 6 | 875957 | 7742
Foam 1/2" | 30 | 2760 | 66.1 | 64.7 | 670 | 905 | 30 | 473 | 6846 | 30 | 4.87 | 6.99 | 30 |  |  | 30 | [6 empty] | 0 | 0 | 878757 | 7765
| average | 2853.3567 | 65.2767 | 61.9733 | 618.9 | 907.5 | average | 570.6437 | 7130.1833 |  | 5.14 | 7.0317 |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| SD | 186.1192 | 2.4223 | 11.3831 | 163.4219 | 962.2145 | SD | 54.5156 | 726.9953 |  | 0.17432 | 0.051333 |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Jun'16
VTCAD June 2016 Operational Data
notes | Day of June 2016 | biogas consumed (m3/day) | CH4 (%) | CH4 (%) 24 hr avg | H2S (ppm) | H2S (ppm) 24 hr avg | day | electricity consumed (kWh/day) | electricity produced (kWh/day) | day | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
1/2" foam | 1 | 2299 | 66.2 | 65.3 | 652 | 841 | 1 | 543 | 5499 | 1 | 4.92 | 7.03 | 1 |  |  | 1 | [6 empty] | 2 | 0 | 884157 | 7812
1" foam | 2 | 2484.8 | 65.9 | 65 | 614 | 805 | 2 | 550.5 | 5671.5 | 2 | 4.74 | 6.97 | 2 |  |  | 2 | [6 empty] | 0 | 8 | 886657 | 7836
1" foam | 3 | 2974.5 | 59.6 | 61.7 | 658 | 841 | 3 | 546.1 | 6466.1 | 3 | 4.72 | 7.02 | 3 |  |  | 3 | [6 empty] | 0 | 0 | 889557 | 7859
1/2" foam | 4 | 2377.8 | 64.8 | 62.7 | 467 | 700 | 4 | 493.1 | 5360.8 | 4 | 4.82 | 6.97 | 4 |  |  | 4 | [6 empty] | 3 | 41 | 891957 | 7878
| 5 | 3099.4 | 65.5 |  | 469 |  | 5 | 517.2 | 7121.6 | 5 | 4.98 | 7.05 | 5 |  |  | 5 | [6 empty] | 0 | 0 | 895157 | 7903
Hydrolsate oily; 1/2 foam | 6 | 2993.3 | 66.1 | 64.3 | 466 | 519 | 6 | 506.9 | 7249 | 6 | 5.03 | 7.01 | 6 |  |  | 6 | [6 empty] | 0 | 0 | 898257 | 7928
| 7 | 2501.6 | 65.6 | 63.3 | 410 | 554 | 7 | 482.8 | 6266.4 | 7 | 5.04 | 7.01 | 7 |  |  | 7 | [6 empty] | 1 | 6 | 900957 | 7950
7:45 | 8 | 2766 | 64.3 | 64.2 | 409 | 538 | 8 | 548 | 6545 | 8 | 4.98 | 7.13 | 8 |  |  | 8 | [6 empty] | 0 | 0 | 903757 | 7974
| 9 | [5 empty] | 9 |  |  | 9 |  |  | 9 |  |  | 9
| 10 | [5 empty] | 10 |  |  | 10 |  |  | 10 |  |  | 10
| 11 | [5 empty] | 11 |  |  | 11 |  |  | 11 |  |  | 11
| 12 | [5 empty] | 12 |  |  | 12 |  |  | 12 |  |  | 12
| 13 | [5 empty] | 13 |  |  | 13 |  |  | 13 |  |  | 13
| 14 | [5 empty] | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 15 | [5 empty] | 15 |  |  | 15 |  |  | 15 |  |  | 15
| 16 | [5 empty] | 16 |  |  | 16 |  |  | 16 |  |  | 16
| 17 | [5 empty] | 17 |  |  | 17 |  |  | 17 |  |  | 17
| 18 | [5 empty] | 18 |  |  | 18 |  |  | 18 |  |  | 18
| 19 | [5 empty] | 19 |  |  | 19 |  |  | 19 |  |  | 19
| 20 | [5 empty] | 20 |  |  | 20 |  |  | 20 |  |  | 20
| 21 | [5 empty] | 21 |  |  | 21 |  |  | 21 |  |  | 21
| 22 | [5 empty] | 22 |  |  | 22 |  |  | 22 |  |  | 22
| 23 | [5 empty] | 23 |  |  | 23 |  |  | 23 |  |  | 23
| 24 | [5 empty] | 24 |  |  | 24 |  |  | 24 |  |  | 24
| 25 | [5 empty] | 25 |  |  | 25 |  |  | 25 |  |  | 25
| 26 | [5 empty] | 26 |  |  | 26 |  |  | 26 |  |  | 26
| 27 | [5 empty] | 27 |  |  | 27 |  |  | 27 |  |  | 27
| 28 | [5 empty] | 28 |  |  | 28 |  |  | 28 |  |  | 28
| 29 | [5 empty] | 29 |  |  | 29 |  |  | 29 |  |  | 29
| 30 | [5 empty] | 30 |  |  | 30 |  |  | 30 |  |  | 30
| average | #DIV/0! | #DIV/0! |  | #DIV/0! |  | average | #DIV/0! | 6272.425 |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | average | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| SD | #DIV/0! | #DIV/0! |  | #DIV/0! |  | SD | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | SD | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!