## counters
| Francois counters |  |  |  |  | 2G |  |  | watertraps |  |  |  | biogas consumed | kwh consumed | kwh produced
date time | biogas consumed m3 | Kwh consumed | Kwh produced | gen count | flare count | cumulative biogas 2G | genset operation hrs | initials | 1 | 2 | notes | hours between recordings | m3/day | /day | /day
2014-06-06 14:13 | [11 empty] | #VALUE! | #REF! | #VALUE! | #VALUE!
2014-06-07 07:15 | [11 empty] | 17.0333 | 0 | 0 | 0
2014-06-09 08:45 | [11 empty] | 49.5 | 0 | 0 | 0
2014-06-11 08:55 | [11 empty] | 48.1667 | 0 | 0 | 0
2014-06-12 11:30 | [11 empty] | 26.5833 | 0 | 0 | 0
2014-06-13 10:00 | [11 empty] | 22.5 | 0 | 0 | 0
2014-06-16 10:00 | [11 empty] | 72 | 0 | 0 | 0
2014-06-17 09:30 | [11 empty] | 23.5 | 0 | 0 | 0
2014-06-18 09:00 | [11 empty] | 23.5 | 0 | 0 | 0
2014-06-19 09:30 | [11 empty] | 24.5 | 0 | 0 | 0
2014-06-20 08:40 | [11 empty] | 23.1667 | 0 | 0 | 0
2014-06-23 10:30 | [11 empty] | 73.8333 | 0 | 0 | 0
2014-06-24 08:30 | [11 empty] | 22 | 0 | 0 | 0
2014-06-25 07:30 | [11 empty] | 23 | 0 | 0 | 0
2014-06-25 13:00 | [11 empty] | 5.5 | 0 | 0 | 0
2014-06-30 10:30 | [11 empty] | 117.5 | 0 | 0 | 0
2014-07-01 07:30 | [11 empty] | 21 | 0 | 0 | 0
2014-07-02 14:30 | [11 empty] | 31 | 0 | 0 | 0
2014-07-03 07:30 | [11 empty] | 17 | 0 | 0 | 0
2014-07-07 08:30 | [11 empty] | 97 | 0 | 0 | 0
2014-07-08 07:30 | [11 empty] | 23 | 0 | 0 | 0
2014-07-09 10:00 | [11 empty] | 26.5 | 0 | 0 | 0
2014-07-10 07:30 | [11 empty] | 21.5 | 0 | 0 | 0
2014-07-11 09:00 | [11 empty] | 25.5 | 0 | 0 | 0
2014-07-14 09:00 | [11 empty] | 72 | 0 | 0 | 0
2014-07-15 07:30 | [11 empty] | 22.5 | 0 | 0 | 0
2014-07-16 07:00 | [11 empty] | 23.5 | 0 | 0 | 0
2014-07-21 09:30 | [11 empty] | 122.5 | 0 | 0 | 0
2014-07-22 08:00 | [11 empty] | 22.5 | 0 | 0 | 0
2014-07-23 08:00 | [11 empty] | 24 | 0 | 0 | 0
2014-07-24 07:30 | [11 empty] | 23.5 | 0 | 0 | 0
2014-07-28 08:00 | [11 empty] | 96.5 | 0 | 0 | 0
2014-07-29 07:30 | [11 empty] | 23.5 | 0 | 0 | 0
2014-07-30 | [11 empty] | 16.5 | 0 | 0 | 0
2014-08-01 14:00 | [11 empty] | 62 | 0 | 0 | 0
2014-08-04 | [11 empty] | 58 | 0 | 0 | 0
2014-08-05 10:00 | [11 empty] | 34 | 0 | 0 | 0
2014-08-06 09:30 | [11 empty] | 23.5 | 0 | 0 | 0
2014-08-07 15:00 | [5 empty] | 1610 | 194 |  |  |  |  | 29.5 | 0 | 0 | 0
2014-08-08 09:00 | [11 empty] | 18 | 0 | 0 | 0
2014-08-12 10:00 | [11 empty] | 97 | 0 | 0 | 0
2014-08-13 07:30 | [11 empty] | 21.5 | 0 | 0 | 0
2014-08-14 13:30 | [11 empty] | 30 | 0 | 0 | 0
2014-08-15 15:45 | [5 empty] | 1940 | 214 |  |  |  |  | 26.25 | 0 | 0 | 0
2014-08-19 14:45 | [5 empty] | 2210 | 238 |  |  |  |  | 95 | 0 | 0 | 0
2014-08-20 15:45 | [5 empty] | 2240 | 241 |  |  |  |  | 25 | 0 | 0 | 0
2014-08-21 | [11 empty] | 8.25 | 0 | 0 | 0
2014-08-22 10:37 | [5 empty] | 2310 | 246 |  |  |  |  | 34.6167 | 0 | 0 | 0
2014-08-25 07:00 | [5 empty] | 2440 | 256 |  |  |  |  | 68.3833 | 0 | 0 | 0
2014-08-26 08:00 | [5 empty] | 2470 | 260 |  |  |  |  | 25 | 0 | 0 | 0
2014-08-27 08:30 | [5 empty] | 2510 | 264 |  |  |  |  | 24.5 | 0 | 0 | 0
2014-08-28 07:30 | [5 empty] | 2540 | 266 |  |  |  |  | 23 | 0 | 0 | 0
2014-08-29 07:30 | [5 empty] | 2590 | 272 |  |  |  |  | 24 | 0 | 0 | 0
2014-09-02 | [11 empty] | 88.5 | 0 | 0 | 0
2014-09-03 | [11 empty] | 24 | 0 | 0 | 0
2014-09-04 10:30 |  |  |  | 1 |  | 2930 | 306 |  |  |  |  | 34.5 | 0 | 0 | 0
2014-09-05 08:30 |  |  |  | 1 |  | 2960 | 309 |  |  |  |  | 22 | 0 | 0 | 0
2014-09-08 07:30 |  |  |  | 14 |  | 3160 | 323 |  |  |  |  | 71 | 0 | 0 | 0
2014-09-09 10:30 |  |  |  | 6 |  | 3250 | 323 |  |  |  |  | 27 | 0 | 0 | 0
2014-09-10 07:00 |  |  |  | 4 |  | 3310 | 333 |  |  |  |  | 20.5 | 0 | 0 | 0
2014-09-11 07:00 |  |  |  | 5 |  | 3390 | 337 |  |  |  |  | 24 | 0 | 0 | 0
2014-09-12 07:00 |  |  |  | 5 |  | 3460 | 342 |  |  |  |  | 24 | 0 | 0 | 0
2014-09-15 09:00 |  |  |  | 13 |  | 3650 | 353 |  |  |  |  | 74 | 0 | 0 | 0
2014-09-16 09:00 |  |  |  | 3 |  | 3690 | 356 |  |  |  |  | 24 | 0 | 0 | 0
2014-09-17 09:00 |  |  |  | 4 |  | 3750 | 360 |  |  |  |  | 24 | 0 | 0 | 0
2014-09-18 09:00 |  |  |  | 4 |  | 3810 | 364 |  |  |  |  | 24 | 0 | 0 | 0
2014-09-19 13:00 |  |  |  | 4 |  | 3870 | 367 |  |  |  |  | 28 | 0 | 0 | 0
2014-09-22 07:30 |  |  |  | 10 |  | 4010 | 376 |  |  |  |  | 66.5 | 0 | 0 | 0
2014-09-23 10:00 |  |  |  | 4 |  | 4070 | 380 |  |  |  |  | 26.5 | 0 | 0 | 0
2014-09-24 09:00 |  |  |  | 4 |  | 4130 | 384 |  |  |  |  | 23 | 0 | 0 | 0
2014-09-25 15:00 | 491 | 404 | 1052 | 6 | 0 | [6 empty] | 30 | 392.8 | 323.2 | 841.6
2014-09-26 11:30 | 635 | 770 | 1363 | 4 | 0 | [6 empty] | 20.5 | 743.4146 | 901.4634 | 1595.7073
2014-09-27 17:00 | 1123 | 674 | 2337 | 7 | 0 | [6 empty] | 29.5 | 913.6271 | 548.339 | 1901.2881
2014-09-28 10:30 | 692 | 352 | 1395 | 5 | 0 | 4460 | [5 empty] | 17.5 | 949.0286 | 482.7429 | 1913.1429
2014-09-29 08:30 | 109 | 475 | 229 | 1 | 16 | 4470 | 404 |  |  |  |  | 22 | 118.9091 | 518.1818 | 249.8182
2014-09-30 07:30 | 0 | 538 | 0 | 0 | 11 | 4470 | 404 |  |  |  |  | 23 | 0 | 561.3913 | 0
2014-10-01 08:00 | 0 | 500 | 0 | 0 | 155 | 4470 | 404 |  |  |  |  | 24.5 | 0 | 489.7959 | 0
2014-10-02 09:00 | 0 | 645 | 0 | 0 | 13 | 4470 | 404 |  |  |  |  | 25 | 0 | 619.2 | 0
2014-10-03 09:00 | 0 | 630 | 0 | 0 | 14 | [6 empty] | 24 | 0 | 630 | 0
2014-10-05 18:37 | 0 |  | 0 | 0 | 53 | [6 empty] | 57.6167 | 0 | 0 | 0
2014-10-06 | 0 |  | 0 | 0 | 78 | [6 empty] | 5.3833 | 0 | 0 | 0
2014-10-07 10:00 | 0 |  | 0 | 0 | [7 empty] | 34 | 0 | 0 | 0
2014-10-08 08:00 | 0 |  | 0 | 0 | [7 empty] | 22 | 0 | 0 | 0
2014-10-09 09:30 | 0 | 2848 | 0 | 0 | 105 | 4470 | 404 |  |  |  |  | 25.5 | 0 | 2680.4706 | 0
2014-10-10 10:00 | [11 empty] | 24.5 | 0 | 0 | 0
2014-10-11 16:00 | 435 | 409 | 1433 | 5 | 0 | [6 empty] | 30 | 348 | 327.2 | 1146.4
2014-10-12 17:45 | 460 | 415 | 1559 | 6 | 0 | [6 empty] | 25.75 | 428.7379 | 386.7961 | 1453.0485
2014-10-13 09:30 | 231 | 229 | 823 | 3 | 3 | 4482 | 416 |  |  |  |  | 15.75 | 352 | 348.9524 | 1254.0952
2014-10-14 09:00 | 969 | 501 | 2330 | 7 | 2 | 4492 | 423 |  |  |  |  | 23.5 | 989.617 | 511.6596 | 2379.5745
2014-10-15 08:24 | [11 empty] | 23.4 | 0 | 0 | 0
2014-10-16 08:30 | 0 | 1086 | 0 | 0 | 54 | 4492 | 423 |  |  |  |  | 24.1 | 0 | 1081.4938 | 0
2014-10-17 08:10 | 0 | 465 | 0 | 0 | 81 | 4492 | 423 |  |  |  |  | 23.6667 | 0 | 471.5493 | 0
2014-10-18 13:15 | [11 empty] | 29.0833 | 0 | 0 | 0
2014-10-19 18:42 | [11 empty] | 29.45 | 0 | 0 | 0
2014-10-20 08:30 | 0 | 1380 | 0 | 0 | 159 | 4492 | 423 |  |  |  |  | 13.8 | 0 | 2400 | 0
2014-10-21 08:30 | 0 | 561 | 0 | 0 | 67 | 4492 | 423 |  |  |  |  | 24 | 0 | 561 | 0
2014-10-22 08:00 | 0 | 445 | 0 | 0 | 120 | 4492 | 423 |  |  |  |  | 23.5 | 0 | 454.4681 | 0
2014-10-23 08:00 | 0 | 437 | 0 | 0 | 66 | 4492 | 423 |  |  |  |  | 24 | 0 | 437 | 0
2014-10-23 16:50 | [11 empty] | 8.8333 | 0 | 0 | 0
2014-10-24 08:30 | 464 | 743 | 1541 | 4 | 50 | 4497 | 428 |  |  |  |  | 15.6667 | 710.8085 | 1138.2128 | 2360.6809
2014-10-25 16:30 | 991 | 727 | 3044 | 9 | 1 | [6 empty] | 32 | 743.25 | 545.25 | 2283
2014-10-26 17:30 | [11 empty] | 25 | 0 | 0 | 0
2014-10-27 07:00 | 1668 | 1385 | 4942 | 14 | 26 | 4514 | 442 |  |  |  |  | 13.5 | 2965.3333 | 2462.2222 | 8785.7778
2014-10-28 08:00 | 418 | 680 | 1126 | 3 | 22 | 4518 | 446 |  |  |  |  | 25 | 401.28 | 652.8 | 1080.96
2014-10-29 11:30 | 647 | 571 | 2084 | 7 | 2 | 4524 | 452 |  |  |  |  | 27.5 | 564.6545 | 498.3273 | 1818.7636
2014-10-30 08:30 | 387 | 476 | 1384 | 4 | 0 | 4528 | 456 |  |  |  |  | 21 | 442.2857 | 544 | 1581.7143
2014-10-31 08:00 | 394 | 611 | 1458 | 4 | 0 | 4532 | 460 |  |  |  |  | 23.5 | 402.383 | 624 | 1489.0213
2014-11-03 07:30 | 1310 | 1583 | 4662 | 19 | 0 | 4546 | 474 |  |  |  |  | 71.5 | 439.7203 | 531.3566 | 1564.8671
2014-11-04 08:00 | 544 | 653 | 1864 | 5 | 0 | 4551 | 479 |  |  |  |  | 24.5 | 532.898 | 639.6735 | 1825.9592
2014-11-05 08:30 | 496 | 622 | 1695 | 11 | 0 | 4556 | 484 |  |  |  |  | 24.5 | 485.8776 | 609.3061 | 1660.4082
2014-11-06 07:30 | 485 | 651 | 1790 | 5 | 0 | 4957 | 490 |  |  |  |  | 23 | 506.087 | 679.3043 | 1867.8261
2014-11-07 07:30 | 547 | 761 | 2035 | 6 | 0 | 5557 | 496 |  |  |  |  | 24 | 547 | 761 | 2035
2014-11-10 07:55 | 2066 | 1787 | 6446 | 18 | 0 | 7657 | 515 |  |  |  |  | 72.4167 | 684.7043 | 592.2394 | 2136.3038
2014-11-11 08:30 | 794 | 697 | 2175 | 11 | 0 | 8457 | 521 |  |  |  |  | 24.5833 | 775.1593 | 680.461 | 2123.3898
2014-11-12 08:15 | 682 | 619 | 1962 | 5 | 0 | 9157 | 527 |  |  |  |  | 23.75 | 689.1789 | 625.5158 | 1982.6526
2014-11-13 07:15 | 594 | 706 | 1837 | 5 | 0 | 9757 | 532 |  |  |  |  | 23 | 619.8261 | 736.6957 | 1916.8696
2014-11-14 08:15 | 511 | 750 | 1673 | 4 | 0 | 10257 | 537 |  |  |  |  | 25 | 490.56 | 720 | 1606.08
2014-11-17 08:30 | 1546 | 1847 | 5192 | 17 | 0 | 11757 | 552 |  |  |  |  | 72.25 | 513.5502 | 613.5363 | 1724.6782
2014-11-18 08:20 | 515 | 635 | 1815 | 10 | 0 | 12357 | 558 |  |  |  |  | 23.8333 | 518.6014 | 639.4406 | 1827.6923
2014-11-19 08:20 | 379 | 798 | 1187 | 9 | 18 | 12657 | 561 |  |  |  |  | 24 | 379 | 798 | 1187
2014-11-20 07:30 | 372 | 552 | 1329 | 4 | 1 | 13057 | 565 |  |  |  |  | 23.1667 | 385.3813 | 571.8561 | 1376.8058
2014-11-21 09:20 | 519 | 835 | 1890 | 10 | 3 | 13557 | 571 |  |  |  |  | 25.8333 | 482.1677 | 775.7419 | 1755.871
2014-11-24 08:40 | 1228 | 1825 | 4255 | 22 | 8 | 14857 | 584 |  |  |  |  | 71.3333 | 413.1589 | 614.0187 | 1431.5888
2014-11-25 08:30 | 461 | 750 | 1680 | 5 | 0 | 15257 | 589 |  |  |  |  | 23.8333 | 464.2238 | 755.2448 | 1691.7483
2014-11-26 09:45 | 325 | 687 | 1089 | 4 | 0 | 15657 | 592 |  |  |  |  | 25.25 | 308.9109 | 652.9901 | 1035.0891
2014-11-28 08:30 | 795 | 1167 | 2461 | 9 | 0 | 16457 | 599 |  |  |  |  | 46.75 | 408.1283 | 599.1016 | 1263.4011
2014-12-01 08:00 | 1070 | 1767 | 3440 | 26 | 8 | 17457 | 610 |  |  |  |  | 71.5 | 359.1608 | 593.1189 | 1154.6853
2014-12-02 08:00 | 285 | 748 | 844 | 9 | 0 | 17757 | 613 |  |  |  |  | 24 | 285 | 748 | 844
2014-12-03 09:50 | 516 | 716 | 1568 | 8 | 0 | 18357 | 617 |  |  |  |  | 25.8333 | 479.3806 | 665.1871 | 1456.7226
2014-12-04 08:00 | 462 | 595 | 1331 | 8 | 6 | 18757 | 621 |  |  |  |  | 22.1667 | 500.2105 | 644.2105 | 1441.0827
2014-12-05 09:15 | 535 | 663 | 1294 | 5 | 2 | 19357 | 625 |  |  |  |  | 25.25 | 508.5149 | 630.1782 | 1229.9406
2014-12-08 11:30 | 1207 | 1784 |  | 15 |  | 20557 | 637 |  |  |  |  | 74.25 | 390.1414 | 576.6465 | 0
2014-12-09 09:30 | 318 | 313 | 1080 | 11 | 33 | 20857 | 640 |  |  |  |  | 22 | 346.9091 | 341.4545 | 1178.1818
2014-12-10 09:30 | 233 | 459 | 608 | 2 | 61 | 21057 | 643 |  |  |  |  | 24 | 233 | 459 | 608
2014-12-11 08:45 | 0 | 575 | 0 | 0 | 96 | 21057 | 643 |  |  |  |  | 23.25 | 0 | 593.5484 | 0
2014-12-12 08:15 | 0 | 635 | 0 | 0 | 125 | 21057 | 643 |  |  |  |  | 23.5 | 0 | 648.5106 | 0
2014-12-14 09:00 | 1392 | 1529 | 4787 | 13 | 0 | 22557 | 657 |  |  |  |  | 48.75 | 685.2923 | 752.7385 | 2356.6769
2014-12-17 08:30 | 1044 | 1050 | 3376 | 10 | 0 | 23657 | 668 |  |  |  |  | 71.5 | 350.4336 | 352.4476 | 1133.2028
2014-12-18 08:00 | 496 | 614 | 1821 | 7 | 0 | 24057 | 672 |  |  |  |  | 23.5 | 506.5532 | 627.0638 | 1859.7447
2014-12-19 10:00 | 779 | 620 | 2054 | 7 | 0 | 24857 | 678 |  |  |  |  | 26 | 719.0769 | 572.3077 | 1896
2014-12-22 08:45 | 1538 | 1625 | 5348 | 16 | 0 | 26457 | 694 |  |  |  |  | 70.75 | 521.7244 | 551.2367 | 1814.1625
2014-12-23 08:00 | 829 | 525 | 2438 | 6 | 0 | 27257 | 701 |  |  |  |  | 23.25 | 855.7419 | 541.9355 | 2516.6452
2014-12-24 09:50 | 1030 | 639 | 2338 | 6 | 0 | 28357 | 708 |  |  |  |  | 25.8333 | 956.9032 | 593.6516 | 2172.0774
2014-12-25 07:50 | 1089 | 437 | 2392 | 6 | 0 | 29457 | 715 |  |  |  |  | 22 | 1188 | 476.7273 | 2609.4545
2014-12-26 08:00 | 909 | 556 | 2517 | 6 | 0 | 30357 | 722 |  |  |  |  | 24.1667 | 902.731 | 552.1655 | 2499.6414
2014-12-29 08:30 | 2267 | 1681 | 8336 | 21 | 2 | 32657 | 746 |  |  |  |  | 72.5 | 750.4552 | 556.469 | 2759.5034
2014-12-30 07:30 | 714 | 471 | 2499 | 7 | 0 | 33357 | 753 |  |  |  |  | 23 | 745.0435 | 491.4783 | 2607.6522
2014-12-31 08:00 | 741 | 568 | 2678 | 6 | 0 | 34157 | 761 |  |  |  |  | 24.5 | 725.8776 | 556.4082 | 2623.3469
2015-01-02 07:45 | 1948 | 1207 | 5821 | 13 | 0 | 36057 | 778 |  |  |  |  | 47.75 | 979.0995 | 606.6597 | 2925.7382
2015-01-05 08:00 | 1950 | 1644 | 5332 | 16 | 93 | 38057 | 793 |  |  |  |  | 72.25 | 647.7509 | 546.1038 | 1771.1834
2015-01-06 08:15 | 916 | 613 | 3275 | 9 | 4 | 38957 | 803 |  |  |  |  | 24.25 | 906.5567 | 606.6804 | 3241.2371
2015-01-07 09:00 | 1595 | 654 | 3614 | 8 | 0 | 40557 | 813 |  |  |  |  | 24.75 | 1546.6667 | 634.1818 | 3504.4848
2015-01-08 07:50 | 494 | 485 | 1172 | 3 | 86 | 41157 | 817 |  |  |  |  | 22.8333 | 519.2409 | 509.781 | 1231.8832
2015-01-09 08:40 | 924 | 542 | 3272 | 8 | 1 | 42057 | 826 |  |  |  |  | 24.8333 | 892.9933 | 523.8121 | 3162.2013
2015-01-10 09:00 | 1014 | 639 | 3314 | 7 | 1 | 43057 | 836 |  |  |  |  | 24.3333 | 1000.1096 | 630.2466 | 3268.6027
2015-01-11 11:20 | 979 | 670 | 3465 | 7 | 0 | 44057 | 846 |  |  |  |  | 26.3333 | 892.2532 | 610.6329 | 3157.9747
2015-01-12 07:39 | 691 | 450 | 9126 | 11 | 5 | 44757 | 852 |  |  |  |  | 20.3167 | 816.2756 | 531.5833 | 10780.5086
2015-01-13 08:00 | 658 | 688 | 3209 | 7 | 1 | 45757 | 862 |  |  |  |  | 24.35 | 648.5421 | 678.1109 | 3162.8747
2015-01-14 08:50 | 886 | 693 | 3137 | 7 | 2 | 46757 | 872 |  |  |  |  | 24.8333 | 856.2685 | 669.745 | 3031.7315
2015-01-15 07:30 | 990 | 539 | 3482 | 7 | 1 | 47657 | 881 |  |  |  |  | 22.6667 | 1048.2353 | 570.7059 | 3686.8235
2015-01-16 09:00 | 923 | 637 | 3271 | 7 | 6 | 48557 | 890 |  |  |  |  | 25.5 | 868.7059 | 599.5294 | 3078.5882
2015-01-17 08:20 | 912 | 550 | 3138 | 7 | 0 | 49457 | 899 |  |  |  |  | 23.3333 | 938.0571 | 565.7143 | 3227.6571
2015-01-18 14:00 | 1138 | 720 | 3513 | 6 | 27 | 50657 | 909 |  |  |  |  | 29.6667 | 920.6292 | 582.4719 | 2841.9775
2015-01-19 08:45 | 423 | 318 | 1419 | 4 | 0 | 51057 | 914 |  |  |  |  | 18.75 | 541.44 | 407.04 | 1816.32
2015-01-20 09:13 | 704 | 427 | 1706 | 5 | 1 | 51757 | 919 |  |  |  |  | 24.4667 | 690.5722 | 418.8556 | 1673.4605
2015-01-22 07:45 | 1026 | 795 | 3024 | 10 | 3 | 52857 | 928 |  |  |  |  | 46.5333 | 529.1691 | 410.0287 | 1559.6562
2015-01-23 08:15 | 555 | 459 | 1896 | 8 | 5 | 53357 | 933 |  |  |  |  | 24.5 | 543.6735 | 449.6327 | 1857.3061
2015-01-24 08:50 | 679 | 514 | 2203 | 9 | 0 | 54057 | 940 |  |  |  |  | 24.5833 | 662.8881 | 501.8034 | 2150.7254
2015-01-25 08:25 | 556 | 514 | 1917 | 8 | 0 | 54657 | 946 |  |  |  |  | 23.5833 | 565.8233 | 523.0813 | 1950.8693
2015-01-26 07:50 | 584 | 562 | 2000 | 8 | 0 | 55257 | 952 |  |  |  |  | 23.4167 | 598.548 | 576 | 2049.8221
2015-01-27 09:30 | 655 | 631 | 2250 | 11 | 0 | 55857 | 959 |  |  |  |  | 25.6667 | 612.4675 | 590.026 | 2103.8961
2015-01-28 09:30 | [11 empty] | 24 | 0 | 0 | 0
2015-01-29 08:00 | 1386 | 1279 | 4768 | 15 | 0 | 57257 | 973 |  |  |  |  | 22.5 | 1478.4 | 1364.2667 | 5085.8667
2015-01-30 08:45 | 742 | 675 | 2524 | 7 | 0 | 58057 | 980 |  |  |  |  | 24.75 | 719.5152 | 654.5455 | 2447.5152
2015-01-31 11:00 | 833 | 744 | 3006 | 9 | 0 | 58857 | 989 |  |  |  |  | 26.25 | 761.6 | 680.2286 | 2748.3429
2015-02-01 08:00 | 743 | 491 | 2466 | 7 | 0 | 59657 | 997 | pf | 1 | 0 |  | 21 | 849.1429 | 561.1429 | 2818.2857
2015-02-02 08:45 | 897 | 596 | 2822 | 16 | 0 | 60557 | 1005 | zn | 2 | 0 |  | 24.75 | 869.8182 | 577.9394 | 2736.4848
2015-02-03 10:15 | 834 | 624 | 2694 | 9 | 0 | 61357 | 1013 | pf | 1 | 0 |  | 25.5 | 784.9412 | 587.2941 | 2535.5294
2015-02-04 14:20 | 916 | 656 | 2910 | 8 | 4 | 62357 | 1021 | zn | 1 | 0 |  | 28.0833 | 782.8131 | 560.6172 | 2486.8843
2015-02-05 08:56 | 485 | 415 | 1706 | 5 | 0 | 62857 | 1026 | zn | 0 | 0 |  | 18.6 | 625.8065 | 535.4839 | 2201.2903
2015-02-06 08:50 | 569 | 578 | 2005 | 8 | 0 | 63357 | 1032 | zn | 1 | 0 |  | 23.9 | 571.3808 | 580.4184 | 2013.3891
2015-02-07 07:45 | 694 | 525 | 2370 | 6 | 0 | 64057 | 1039 | zn | 1 | 0 |  | 22.9167 | 726.8073 | 549.8182 | 2482.0364
2015-02-08 07:45 | 548 | 538 | 1930 | 6 | 0 | 64657 | 1045 | zn | 0 | 0 |  | 24 | 548 | 538 | 1930
2015-02-09 11:50 | 485 | 682 | 1655 | 5 | 34 | 65157 | 1050 | jp | 1 | 0 |  | 28.0833 | 414.4807 | 582.8368 | 1414.362
2015-02-10 09:36 | 862 | 549 | 2776 | 8 | 0 | 66057 | 1058 | pf | 1 | 0 |  | 21.7667 | 950.4441 | 605.3292 | 3060.827
2015-02-11 08:53 | 807 | 576 | 2858 | 6 | 0 | 66857 | 1066 | jp | 1 | 0 |  | 23.2833 | 831.8397 | 593.7294 | 2945.9699
2015-02-12 07:40 | 1206 | 565 | 3320 | 9 | 4 | 68057 | 1076 | pf | 1 | 0 |  | 22.7833 | 1270.4023 | 595.1719 | 3497.2933
2015-02-13 08:00 | 1661 | 753 | 3618 | 11 | 1 | 69757 | 1086 | zn | 1 | 1 |  | 24.3333 | 1638.2466 | 742.6849 | 3568.4384
2015-02-14 09:15 | 1598 | 740 | 3300 | 7 | 6 | 71357 | 1096 | jp | 2 | 0 |  | 25.25 | 1518.8911 | 703.3663 | 3136.6337
2015-02-15 09:20 | 190 | 558 | 415 | 1 | 39 | 71557 | 1097 | jp | 0 | 1 |  | 24.0833 | 189.3426 | 556.0692 | 413.564
2015-02-16 09:20 | 728 | 557 | 2695 | 6 | 5 | 72257 | 1105 | jp | 0 | 0 |  | 24 | 728 | 557 | 2695
2015-02-17 08:20 | 174 | 662 | 628 | 2 | 168 | 72457 | 1107 | pf | 1 | 0 |  | 23 | 181.5652 | 690.7826 | 655.3043
2015-02-18 10:24 | 1492 | 754 | 3895 | 7 | 0 | 73957 | 1118 | zn | 1 | 0 |  | 26.0667 | 1373.7084 | 694.2199 | 3586.1893
2015-02-19 08:47 | 1303 | 555 | 2843 | 8 | 2 | 75257 | 1126 | zn | 2 | 0 |  | 22.3833 | 1397.1109 | 595.0856 | 3048.3395
2015-02-20 09:30 | 1400 | 654 | 2948 | 7 | 6 | 76757 | 1134 | pf | 1 | 0 |  | 24.7167 | 1359.4066 | 635.0371 | 2862.5219
2015-02-21 07:41 | 1297 | 722 | 2768 | 9 | 0 | 78057 | 1143 | zn | 1 | 0 |  | 22.1833 | 1403.2156 | 781.127 | 2994.6807
2015-02-22 07:50 | 1587 | 648 | 3471 | 9 | 1 | 79657 | 1153 | zn | 1 | 0 |  | 24.15 | 1577.1429 | 643.9752 | 3449.441
2015-02-23 08:13 | 1324 | 579 | 3039 | 8 | 0 | 80957 | 1161 | zn | 2 | 0 |  | 24.3833 | 1303.1852 | 569.8975 | 2991.2235
2015-02-24 | [11 empty] | 15.7833 | 0 | 0 | 0
2015-02-25 08:15 | 3523 | 1300 | 7830 | 18 | 14 | 84557 | 1184 | jp | 2 | 1 |  | 32.25 | 2621.7674 | 967.4419 | 5826.9767
2015-02-26 14:36 | 778 | 895 | 1965 | 3 | 220 | 85357 | 1189 | pf | 1 | 0 |  | 30.35 | 615.2224 | 707.743 | 1553.8715
2015-02-27 09:00 | 1069 | 411 | 3324 | 7 | 5 | 86457 | 1199 | jp | 2 | 0 |  | 18.4 | 1394.3478 | 536.087 | 4335.6522
2015-02-28 08:30 | 1222 | 585 | 4297 | 9 | 0 | 87657 | 1211 | pf | 2 | 1 |  | 23.5 | 1248 | 597.4468 | 4388.4255
2015-03-01 08:40 | 1312 | 577 | 4876 | 9 | 0 | 88957 | 1225 | zn | 2 | 0 |  | 24.1667 | 1302.9517 | 573.0207 | 4842.3724
2015-03-02 09:00 | 1223 | 571 | 4593 | 8 | 0 | 90257 | 1238 | jp | 4 | 0 |  | 24.3333 | 1206.2466 | 563.1781 | 4530.0822
2015-03-03 12:00 | 1592 | 921 | 5336 | 9 | 0 | 91857 | 1253 | pf | 3 | 0 |  | 27 | 1415.1111 | 818.6667 | 4743.1111
2015-03-04 08:40 | 1826 | 511 | 3950 | 7 | 0 | 93657 | 1265 | jp | 2 | 0 |  | 20.6667 | 2120.5161 | 593.4194 | 4587.0968
2015-03-05 08:28 | 2097 | 682 | 4685 | 8 | 0 | 95757 | 1278 | zn | 3 | 0 |  | 23.8 | 2114.6218 | 687.7311 | 4724.3697
2015-03-06 08:15 | 2103 | 613 | 4605 | 8 | 0 | 97957 | 1291 | zn | 1 | 0 |  | 23.7833 | 2122.1584 | 618.5844 | 4646.9516
2015-03-07 09:50 | 2012 | 757 | 4783 | 9 | 0 | 99957 | 1305 | zn | 2 | 0 |  | 25.5833 | 1887.4788 | 710.1498 | 4486.9837
2015-03-08 08:15 | 1842 | 513 | 4355 | 7 | 0 | 101857 | 1317 | zn | 2 | 0 |  | 22.4167 | 1972.1041 | 549.2342 | 4662.6022
2015-03-09 09:00 | 2340 | 680 | 5359 | 8 | 0 | 104157 | 1332 | jp | 5 | 0 |  | 24.75 | 2269.0909 | 659.3939 | 5196.6061
2015-03-10 07:45 | 1991 | 696 | 4731 | 7 | 0 | 106257 | 1345 | zn | 2 | 0 |  | 22.75 | 2100.3956 | 734.2418 | 4990.9451
2015-03-11 07:32 | 1843 | 623 | 4046 | 7 | 0 | 108057 | 1357 | zn | 5 | 1 |  | 23.7833 | 1859.7898 | 628.6755 | 4082.8591
2015-03-12 07:08 | 1879 | 587 | 4218 | 8 | 0 | 109957 | 1369 | zn | 3 | 0 |  | 23.6 | 1910.8475 | 596.9492 | 4289.4915
2015-03-13 08:50 | 958 | 770 | 2653 | 5 | 0 | 110579 | 1377 | zn | 1 | 0 | genset off sometime during night, electrical connection came undone | 25.7 | 894.6304 | 719.0661 | 2477.5097
2015-03-14 10:00 | 2511 | 673 | 6184 | 7 | 0 | 113457 | 1394 | jp | 5 | 0 |  | 25.1667 | 2394.596 | 641.8013 | 5897.3245
2015-03-15 08:35 | 2366 | 541 | 5141 | 7 | 0 | 115857 | 1408 | jp | 5 | 0 |  | 22.5833 | 2514.4207 | 574.9373 | 5463.4982
2015-03-16 08:45 | 2896 | 654 | 6911 | 5 | 0 | 118857 | 1428 | zn | 5 | 0 |  | 24.1667 | 2876.0276 | 649.4897 | 6863.3379
2015-03-17 08:30 | 3163 | 715 | 6742 | 6 | 0 | 122057 | 1446 | pf | 5 | 0 |  | 23.75 | 3196.2947 | 722.5263 | 6812.9684
2015-03-18 08:30 | 2211 | 734 | 6043 | 8 | 0 | 124257 | 1463 | zn | 4 | 0 |  | 24 | 2211 | 734 | 6043
2015-03-19 08:00 | 1788 | 569 | 6645 | 6 | 0 | 126057 | 1482 | zn | 3 | 0 |  | 23.5 | 1826.0426 | 581.1064 | 6786.383
2015-03-20 09:21 | 2448 | 740 | 8320 | 5 | 0 | 124557 | 1504 | jp | 4 | 0 |  | 25.35 | 2317.6331 | 700.5917 | 7876.9231
2015-03-21 09:00 | 2138 | 714 | 7771 | 5 | 0 | 130757 | 1523 | pf | 5 | 0 |  | 23.65 | 2169.6406 | 724.5666 | 7886.0042
2015-03-22 08:10 | 1913 | 580 | 7195 | 4 | 0 | 132657 | 1545 | pf | 5 | 0 | approx. 5 pm feedrate to digester changed to 1100gal/2hr | 23.1667 | 1981.8129 | 600.8633 | 7453.8129
2015-03-23 08:20 | 1820 | 632 | 6941 | 2 | 0 | 134557 | 1564 | zn | 3 | 0 | genset off between 3 am and 6:45 am. Likely a power surge shut it down | 24.1667 | 1807.4483 | 627.6414 | 6893.131
2015-03-24 08:15 | 2205 | 660 | 8525 | 1 | 0 | 136757 | 1587 | pf | 6 | 0 | dig. Feedrate set back to 1000/2hrs Monday afternoon- genset not keeping up with gas production | 23.9167 | 2212.6829 | 662.2997 | 8554.7038
2015-03-25 09:05 | 2403 | 700 | 9341 | 0 | 0 | 139257 | 1613 | jp | 6 | 0 |  | 24.8333 | 2322.3624 | 676.5101 | 9027.5436
2015-03-26 08:12 | 2055 | 567 | 7701 | 1 | 0 | 141357 | 1633 | pf | 6 | 0 |  | 23.1167 | 2133.5256 | 588.6662 | 7995.2704
2015-03-27 08:07 | 2426 | 630 | 6500 | 1 | 0 | 143757 | 1651 | zn | 6 | 0 |  | 23.9167 | 2434.453 | 632.1951 | 6522.6481
2015-03-28 08:15 | 2830 | 650 | 8104 | 1 | 0 | 146657 | 1674 | jp | 6 | 0 |  | 24.1333 | 2814.3646 | 646.4088 | 8059.2265
2015-03-29 08:30 | 2642 | 584 | 8186 | 1 | 0 | 149357 | 1698 | jp | 5 | 0 |  | 24.25 | 2614.7629 | 577.9794 | 8101.6082
2015-03-30 09:23 | 2294 | 587 | 7572 | 3 | 0 | 151657 | 1720 | zn | 5 | 0 |  | 24.8833 | 2212.5653 | 566.1621 | 7303.2016
2015-03-31 08:05 | 1982 | 648 | 6883 | 2 | 0 | 153657 | 1739 | zn | 4 | 0 |  | 22.7 | 2095.5066 | 685.1101 | 7277.1806
2015-04-01 08:13 | 2794 | 712 | 8489 | 0 | 0 | 156457 | 1763 | zn | 4 | 0 |  | 24.1333 | 2778.5635 | 708.0663 | 8442.0994
2015-04-02 08:49 | 3003 | 762 | 8614 | 0 | 0 | 159557 | 1788 | pf | 5 | 0 |  | 24.6 | 2929.7561 | 743.4146 | 8403.9024
2015-04-04 07:50 | 4356 | 1170 | 13907 | 3 | 0 | 163957 | 1828 | zn | 11 | 0 |  | 47.0167 | 2223.5519 | 597.235 | 7098.9295
2015-04-06 08:49 | 5298 | 1240 | 15706 | 6 | 0 | 169257 | 1873 | jp | 8 | 0 |  | 48.9833 | 2595.8217 | 607.5536 | 7695.3522
2015-04-07 08:10 | 2519 | 612 | 7487 | 3 | 0 | 171957 | 1895 | zn | 4 | 0 |  | 23.35 | 2589.1221 | 629.0364 | 7695.4176
2015-04-08 08:10 | 2544 | 659 | 7582 | 3 | 0 | 174457 | 1916 | zn | 4 | 0 |  | 24 | 2544 | 659 | 7582
2015-04-09 08:46 | 2471 | 727 | 7734 | 4 | 0 | 176957 | 1938 | zn | 5 | 0 |  | 24.6 | 2410.7317 | 709.2683 | 7545.3659
2015-04-10 08:06 | 2047 | 605 | 6799 | 5 | 0 | 179057 | 1958 | zn | 3 | 0 |  | 23.3333 | 2105.4857 | 622.2857 | 6993.2571
2015-04-11 09:09 | 1678 | 705 | 6197 | 6 | 8 | 180575 | 1976 | pf | 3 | 0 |  | 25.05 | 1607.6647 | 675.4491 | 5937.2455
2015-04-12 11:00 | 1821 | 690 | 6417 | 9 | 0 | 182157 | 1995 | pf | 4 | 0 |  | 25.85 | 1690.677 | 640.619 | 5957.7563
2015-04-13 08:05 | 1384 | 538 | 4938 | 9 | 0 | 183957 | 2010 | zn | 3 | 0 |  | 21.0833 | 1575.4625 | 612.4269 | 5621.1225
2015-04-14 08:30 | 1559 | 633 | 5679 | 6 | 0 | 185557 | 2027 | zn | 5 | 0 |  | 24.4167 | 1532.3959 | 622.198 | 5582.0887
2015-04-15 08:00 | 1468 | 681 | 5429 | 6 | 0 | 187057 | 2043 | zn | 4 | 0 |  | 23.5 | 1499.234 | 695.4894 | 5544.5106
2015-04-16 11:05 | 1632 | 825 | 5812 | 8 | 0 | 188657 | 2060 | zn | 4 | 0 |  | 27.0833 | 1446.2031 | 731.0769 | 5150.3262
2015-04-17 08:00 | 1213 | 482 | 4434 | 7 | 0 | 189957 | 2073 | pf | 4 | 0 |  | 20.9167 | 1391.8088 | 553.0518 | 5087.6175
2015-04-18 08:30 | 1474 | 724 | 4911 | 7 | 0 | 191475 | 2087 | zn | 5 | 0 |  | 24.5 | 1443.9184 | 709.2245 | 4810.7755
2015-04-19 08:30 | 1392 | 613 | 4825 | 8 | 0 | 192857 | 2102 | zn | 3 | 0 |  | 24 | 1392 | 613 | 4825
2015-04-20 08:20 | 1197 | 660 | 4361 | 8 | 0 | 194057 | 2115 | zn | 4 | 0 |  | 23.8333 | 1205.3706 | 664.6154 | 4391.4965
2015-04-21 08:15 | 1258 | 596 | 4019 | 8 | 2 | 195357 | 2127 | zn | 3 | 0 |  | 23.9167 | 1262.3833 | 598.0767 | 4033.0035
2015-04-22 08:40 | 1710 | 591 | 3745 | 9 | 1 | 197057 | 2138 | jp | 2 | 0 |  | 24.4167 | 1680.8191 | 580.9147 | 3681.0922
2015-04-23 08:20 | 1714 | 723 | 3936 | 9 | 0 | 198557 | 2150 | pf | 3 | 0 |  | 23.6667 | 1738.1408 | 733.1831 | 3991.4366
2015-04-24 08:15 | 1434 | 708 | 3880 | 8 | 4 | 200257 | 2162 | zn | 3 | 0 |  | 23.9167 | 1438.9965 | 710.4669 | 3893.5192
2015-04-25 08:30 | 1328 | 719 | 4092 | 9 | 4 | 201557 | 2174 | jp | 2 | 0 |  | 24.25 | 1314.3093 | 711.5876 | 4049.8144
2015-04-26 08:40 | 1310 | 654 | 4096 | 9 | 6 | 202957 | 2186 | jp | 3 | 0 |  | 24.1667 | 1300.9655 | 649.4897 | 4067.7517
2015-04-27 08:25 | 1294 | 582 | 3587 | 8 | 1 | 204257 | 2197 | zn | 2 | 0 |  | 23.75 | 1307.6211 | 588.1263 | 3624.7579
2015-04-28 08:10 | 1339 | 724 | 3849 | 9 | 0 | 205557 | 2209 | pf | 5 | 0 | AD vertical pump (6) out to replace pump 5 | 23.75 | 1353.0947 | 731.6211 | 3889.5158
2015-04-29 08:30 | 1715 | 736 | 4457 | 8 | 0 | 207357 | 2222 | zn | 3 | 0 |  | 24.3333 | 1691.5068 | 725.9178 | 4395.9452
2015-04-30 08:15 | 1541 | 594 | 4200 | 9 | 0 | 208857 | 2235 | pf | 4 | 0 |  | 23.75 | 1557.2211 | 600.2526 | 4244.2105
2015-05-01 10:52 | 1876 | 770 | 4476 | 9 | 0 | 210757 | 2248 | zn | 3 | 0 | genset turned off and on extra during maintenance and troubleshooting | 26.6167 | 1691.5717 | 694.3018 | 4035.9674
2015-05-02 10:00 | 1869 | 618 | 4709 | 9 | 0 | 212657 | 2262 | jp | 4 | 0 |  | 23.1333 | 1939.0202 | 641.1527 | 4885.4179
2015-05-03 09:00 | 1674 | 566 | 4808 | 8 | 0 | 214357 | 2275 | jp | 4 | 0 |  | 23 | 1746.7826 | 590.6087 | 5017.0435
2015-05-06 08:50 | 4863 | 1935 | 14968 | 26 | 2 | 219257 | 2318 | zn | 15 | 0 |  | 71.8333 | 1624.761 | 646.4965 | 5000.9095
2015-05-07 08:41 | 1604 | 668 | 5654 | 8 | 0 | 220957 | 2334 | zn | 6 | 0 |  | 23.85 | 1614.0881 | 672.2013 | 5689.5597
2015-05-08 09:19 | 1637 | 640 | 5566 | 9 | 1 | 222557 | 2350 | zn | 6 | 0 |  | 24.6333 | 1594.912 | 623.5453 | 5422.8958
2015-05-10 09:20 | 3285 | 1163 | 10463 | 17 | 0 | 225857 | 2379 | zn | 11 | 0 |  | 48.0167 | 1641.9299 | 581.2982 | 5229.6841
2015-05-11 09:24 | 2143 | 563 | 4959 | 9 | 0 | 228157 | 2394 | zn | 5 | 0 |  | 24.0667 | 2137.0637 | 561.4404 | 4945.2632
2015-05-12 08:30 | 1812 | 534 | 4265 | 9 | 6 | 229957 | 2406 | zn | 4 | 0 |  | 23.1 | 1882.5974 | 554.8052 | 4431.1688
2015-05-13 08:40 | 1361 | 633 | 3053 | 6 | 1 | 231257 | 2415 | zn | 3 | 0 |  | 24.1667 | 1351.6138 | 628.6345 | 3031.9448
2015-05-14 09:10 | 1744 | 502 | 4507 | 9 | 0 | 233057 | 2428 | zn | 4 | 0 |  | 24.5 | 1708.4082 | 491.7551 | 4415.0204
2015-05-15 08:46 | 1754 | 617 | 4374 | 8 | 0 | 234857 | 2440 | zn | 4 | 0 |  | 23.6 | 1783.7288 | 627.4576 | 4448.1356
2015-05-16 08:18 | 1926 | 500 | 4220 | 9 | 0 | 236757 | 2452 | zn | 4 | 0 |  | 23.5333 | 1964.1926 | 509.915 | 4303.6827
2015-05-17 | [11 empty] | 15.7 | 0 | 0 | 0
2015-05-18 08:03 | 5675 | 1613 | 12271 | 27 | 0 | 240557 | 2475 | bb | 8 | 0 |  | 32.05 | 4249.61 | 1207.8627 | 9188.8924
2015-05-19 08:30 | 1906 | 608 | 4108 | 9 | 0 | 242557 | 2987 | bb | 4 | 0 |  | 24.45 | 1870.9202 | 596.8098 | 4032.3926
2015-05-21 08:15 | 3870 | 1093 | 8358 | 18 | 1 | 246457 | 2511 | zn | 8 | 0 |  | 47.75 | 1945.1309 | 549.3613 | 4200.8796
2015-05-22 08:00 | 2031 | 491 | 4371 | 10 | 0 | 248457 | 2524 | zn | 4 | 0 |  | 23.75 | 2052.3789 | 496.1684 | 4417.0105
2015-05-23 08:00 | 1579 | 532 | 4566 | 9 | 0 | 250057 | 2537 | zn | 4 | 2 |  | 24 | 1579 | 532 | 4566
2015-05-24 08:05 | 1353 | 580 | 5158 | 8 | 6 | 251457 | 2552 | zn | 5 | 0 | gen switch tripped overnight | 24.0833 | 1348.3183 | 577.9931 | 5140.1522
2015-05-25 08:15 | 1546 | 508 | 6073 | 7 | 0 | 253057 | 2569 | zn | 6 | 0 |  | 24.1667 | 1535.3379 | 504.4966 | 6031.1172
2015-05-26 08:15 | 1536 | 530 | 5710 | 8 | 0 | 254557 | 2585 | zn | 7 | 0 |  | 24 | 1536 | 530 | 5710
2015-05-27 08:20 | 2186 | 592 | 5462 | 9 | 0 | 256757 | 2600 | zn | 7 | 0 |  | 24.0833 | 2178.436 | 589.9516 | 5443.1003
2015-05-28 08:15 | 1743 | 436 | 4799 | 7 | 11 | 258557 | 2614 | bb | 6 | 0 |  | 23.9167 | 1749.0732 | 437.5192 | 4815.7213
2015-05-29 08:18 | 1788 | 542 | 5426 | 9 | 0 | 260357 | 2629 | zn | 6 | 0 |  | 24.05 | 1784.2827 | 540.8732 | 5414.7193
2015-05-30 08:07 | 584 | 540 | 1946 | 3 | 4 | 260957 | 2635 | dr | 3 | 0 |  | 23.8167 | 588.4955 | 544.1568 | 1960.9797
2015-05-31 07:15 | 1693 | 512 | 5122 | 9 | 0 | 262657 | 2649 | dr | 6 | 0 |  | 23.1333 | 1756.4265 | 531.1816 | 5313.8905
2015-06-01 08:00 | 1276 | 521 | 4906 | 9 | 0 | 263957 | 2663 | dr | 5 | 0 |  | 24.75 | 1237.3333 | 505.2121 | 4757.3333
2015-06-02 08:15 | 810 | 585 | 3019 | 7 | 5 | 264757 | 2672 | bb | 2 | 0 |  | 24.25 | 801.6495 | 578.9691 | 2987.8763
2015-06-04 08:15 | 1098 | 494 | 4222 | 9 | 1 | 267257 | 2698 | zn | 4 | 0 |  | 48 | 549 | 247 | 2111
2015-06-05 08:43 | 708 | 551 | 2723 | 5 | 4 | 267257 | 2706 | zn | 3 | 0 | gen switch tripped 8:30 pm | 24.4667 | 694.4959 | 540.4905 | 2671.0627
2015-06-06 08:30 | 1133 | 554 | 4156 | 9 | 0 | 269151 | 2718 | bb | 4 | 0 |  | 23.7833 | 1143.3217 | 559.047 | 4193.8612
2015-06-07 09:00 | 838 | 550 | 3232 | 7 | 1 | 269957 | 2727 | bb | 3 | 0 |  | 24.5 | 820.898 | 538.7755 | 3166.0408
2015-06-08 07:39 | 678 | 427 | 2520 | 6 | 4 | 270657 | 2734 | dr | 3 | 0 |  | 22.65 | 718.4106 | 452.4503 | 2670.1987
2015-06-09 07:30 | 1167 | 605 | 3331 | 7 | 0 | 271857 | 2744 | dr | 3 | 0 |  | 23.85 | 1174.3396 | 608.805 | 3351.9497
2015-06-10 07:52 | 1017 | 553 | 2414 | 6 | 2 | 272857 | 2751 | dr | 2 | 0 |  | 24.3667 | 1001.6963 | 544.6785 | 2377.6744
2015-06-11 08:32 | 1515 | 594 | 3640 | 9 | 1 | 274357 | 2762 | zn | 5 | 0 |  | 24.6667 | 1474.0541 | 577.9459 | 3541.6216
2015-06-12 08:50 | 1035 | 582 | 2993 | 11 | 7 | 275457 | 2771 | bb | 3 | 0 |  | 24.3 | 1022.2222 | 574.8148 | 2956.0494
2015-06-13 07:20 | 1299 | 502 | 3023 | 7 | 1 | 276757 | 2780 | dr | 3 | 0 |  | 22.5 | 1385.6 | 535.4667 | 3224.5333
2015-06-14 07:31 | 605 | 543 | 1863 | 5 | 13 | 277357 | 2785 | dr | 2 | 0 |  | 24.1833 | 600.4135 | 538.8835 | 1848.8766
2015-06-15 11:10 | 1064 | 713 | 3372 | 8 | 0 | 278457 | 2795 | zn | 5 | 0 |  | 27.65 | 923.5443 | 618.8788 | 2926.8716
2015-06-16 08:14 | 875 | 441 | 2271 | 7 | 0 | 279357 | 2802 | zn | 2 | 0 |  | 21.0667 | 996.8354 | 502.4051 | 2587.2152
2015-06-17 07:30 | 1032 | 599 | 2507 | 7 | 1 | 280357 | 2809 | dr | 2 | 0 |  | 23.2667 | 1064.5272 | 617.8797 | 2586.0172
2015-06-18 08:29 | 1035 | 679 | 2990 | 8 | 0 | 281457 | 2818 | zn | 4 | 0 |  | 24.9833 | 994.2628 | 652.2748 | 2872.3149
2015-06-19 08:45 | 1252 | 575 | 2908 | 8 | 0 | 282757 | 2827 | bb | 3 | 0 |  | 24.2667 | 1238.2418 | 568.6813 | 2876.044
2015-06-20 08:15 | 916 | 544 | 2684 | 7 | 0 | 283657 | 2835 | zn | 4 | 1 |  | 23.5 | 935.4894 | 555.5745 | 2741.1064
2015-06-21 09:30 | 1182 | 432 | 2921 | 8 | 0 | 284857 | 2844 | zn | 3 | 0 |  | 25.25 | 1123.4851 | 410.6139 | 2776.396
2015-06-22 08:30 | 1105 | 352 | 2424 | 7 | 0 | 285957 | 2851 | zn | 3 | 0 |  | 23 | 1153.0435 | 367.3043 | 2529.3913
2015-06-23 07:50 | 1103 | 370 | 2414 | 7 | 0 | 287057 | 2858 | dr | 3 | 0 |  | 23.3333 | 1134.5143 | 380.5714 | 2482.9714
2015-06-24 07:50 | 1161 | 374 | 2514 | 7 | 0 | 288257 | 2866 | dr | 3 | 0 |  | 24 | 1161 | 374 | 2514
2015-06-25 07:50 | 1092 | 384 | 2534 | 8 | 0 | 289357 | 2873 | dr | 3 | 0 |  | 24 | 1092 | 384 | 2534
2015-06-26 08:16 | 1147 | 397 | 2679 | 7 | 0 | 290557 | 2881 | zn | 3 | 0 |  | 24.4333 | 1126.6576 | 389.9591 | 2631.487
2015-06-27 08:45 | 1152 | 393 | 2692 | 8 | 0 | 291757 | 2890 | dk | 2 | 0 |  | 24.4833 | 1129.258 | 385.2417 | 2638.8564
2015-06-28 08:00 | 1047 | 388 | 2304 | 7 | 0 | 292857 | 2897 | dk | 3 | 0 |  | 23.25 | 1080.7742 | 400.5161 | 2378.3226
2015-06-29 09:00 | 1211 | 480 | 2707 | 7 | 0 | 293957 | 2904 | bb | 3 | 0 |  | 25 | 1162.56 | 460.8 | 2598.72
2015-06-30 07:59 | 935 | 392 | 2027 | 6 | 0 | 294957 | 2910 | zn | 2 | 0 |  | 22.9833 | 976.3597 | 409.3401 | 2116.6642
2015-07-01 08:20 | 589 | 458 | 1263 | 4 | 6 | 295557 | 2914 | zn | 1 | 0 |  | 24.35 | 580.5339 | 451.4168 | 1244.846
2015-07-02 08:12 | 1082 | 416 | 2327 | 7 | 0 | 296657 | 2921 | zn | 3 | 0 |  | 23.8667 | 1088.0447 | 418.324 | 2340
2015-07-03 08:30 | 1271 | 415 | 2745 | 8 | 0 | 297957 | 2929 | zn | 3 | 0 |  | 24.3 | 1255.3086 | 409.8765 | 2711.1111
2015-07-04 07:00 | 1095 | 409 | 2271 | 7 | 0 | 298957 | 2936 | dk | 3 | 0 |  | 22.5 | 1168 | 436.2667 | 2422.4
2015-07-05 07:17 | 1059 | 423 | 2248 | 7 | 0 | 300057 | 2943 | dr | 3 | 0 |  | 24.2833 | 1046.6438 | 418.0645 | 2221.7708
2015-07-06 08:30 | 1193 | 429 | 2545 | 8 | 0 | 301257 | 2951 | dr | 3 | 0 |  | 25.2167 | 1135.4395 | 408.3014 | 2422.2075
2015-07-07 08:30 | 513 | 401 | 1096 | 4 | 5 | 301857 | 2954 | dr | 4 | 0 |  | 24 | 513 | 401 | 1096
2015-07-08 08:30 | 940 | 464 | 1965 | 6 | 0 | 302757 | 2960 | dr | 3 | 0 |  | 24 | 940 | 464 | 1965
2015-07-09 08:00 | 440 | 451 | 905 | 3 | 4 | 303257 | 2963 | zn | 1 | 0 |  | 23.5 | 449.3617 | 460.5957 | 924.2553
2015-07-10 08:11 | 944 | 487 | 1988 | 7 | 0 | 304157 | 2969 | zn | 2 | 0 |  | 24.1833 | 936.8436 | 483.3081 | 1972.929
2015-07-11 09:20 | 1001 | 609 | 2167 | 7 | 0 | 305157 | 2976 | bb | 3 | 0 |  | 25.15 | 955.2286 | 581.1531 | 2067.9125
2015-07-12 11:15 | 1191 | 530 | 2568 | 8 | 0 | 306357 | 2983 | bb | 3 | 0 |  | 25.9167 | 1102.9196 | 490.8039 | 2378.0836
2015-07-13 07:30 | 948 | 299 | 2028 | 7 | 0 | 307357 | 2990 | dr | 3 | 0 |  | 20.25 | 1123.5556 | 354.3704 | 2403.5556
2015-07-14 08:28 | 1154 | 520 | 2914 | 8 | 0 | 308557 | 2998 | zn | 6 | 0 |  | 24.9667 | 1109.3191 | 499.8665 | 2801.1749
2015-07-15 08:15 | 802 | 496 | 2929 | 7 | 0 | 309357 | 3007 | zn | 3 | 0 |  | 23.7833 | 809.3062 | 500.5186 | 2955.6833
2015-07-16 08:00 | 710 | 507 | 2695 | 7 | 0 | 310057 | 3015 | bb | 2 | 0 |  | 23.75 | 717.4737 | 512.3368 | 2723.3684
2015-07-17 08:08 | 560 | 404 | 2069 | 6 | 0 | 310657 | 3021 | zn | 2 | 0 |  | 24.1333 | 556.9061 | 401.768 | 2057.5691
2015-07-18 08:30 | 790 | 537 | 2583 | 8 | 0 | 311457 | 3029 | bb | 2 | 0 |  | 24.3667 | 778.1122 | 528.9193 | 2544.1313
2015-07-19 08:20 | 1054 | 406 | 2351 | 6 | 0 | 312457 | 3036 | bb | 3 | 0 |  | 23.8333 | 1061.3706 | 408.8392 | 2367.4406
2015-07-20 07:50 | 1077 | 416 | 2367 | 7 | 0 | 313557 | 3043 | dr | 2 | 0 |  | 23.5 | 1099.9149 | 424.8511 | 2417.3617
2015-07-21 08:20 | 1113 | 565 | 2502 | 7 | 0 | 314757 | 3050 | zn | 3 | 0 |  | 24.5 | 1090.2857 | 553.4694 | 2450.9388
2015-07-23 08:12 | 1985 | 900 | 4265 | 13 | 0 | 316757 | 3063 | zn | 5 | 0 |  | 47.8667 | 995.2646 | 451.2535 | 2138.4401
2015-07-24 07:35 | 913 | 416 | 1966 | 6 | 0 | 317657 | 3069 | dr | 2 | 1 |  | 23.3833 | 937.0777 | 426.9708 | 2017.8475
2015-07-25 08:00 | 1079 | 669 | 2336 | 7 | 0 | 318757 | 3076 | zn | 1 | 0 |  | 24.4167 | 1060.587 | 657.5836 | 2296.1365
2015-07-26 07:50 | 833 | 633 | 1794 | 6 | 0 | 319557 | 3082 | zn | 2 | 0 |  | 23.8333 | 838.8252 | 637.4266 | 1806.5455
2015-07-27 07:35 | 1012 | 673 | 2164 | 7 | 0 | 320657 | 3088 | dr | 2 | 0 |  | 23.75 | 1022.6526 | 680.0842 | 2186.7789
2015-07-28 08:28 | 1088 | 686 | 2324 | 7 | 0 | 321757 | 3095 | zn | 3 | 0 |  | 24.8833 | 1049.3771 | 661.6477 | 2241.5003
2015-07-29 11:00 | 1022 | 696 | 2187 | 7 | 0 | 322757 | 31023 | zn | 3 | 0 |  | 26.5333 | 924.4221 | 629.5477 | 1978.191
2015-07-30 08:00 | 724 | 491 | 1545 | 5 | 0 | 323457 | 3106 | dr | 2 | 0 |  | 21 | 827.4286 | 561.1429 | 1765.7143
2015-07-31 08:00 | 880 | 653 | 1881 | 6 | 0 | 324357 | 3112 | dr | 2 | 0 |  | 24 | 880 | 653 | 1881
2015-08-01 07:40 | 902 | 652 | 1939 | 6 | 0 | 325257 | 3118 | dr | 3 | 0 |  | 23.6667 | 914.7042 | 661.1831 | 1966.3099
2015-08-02 07:35 | 1044 | 680 | 2254 | 7 | 0 | 326357 | 3125 | dr | 2 | 0 |  | 23.9167 | 1047.6376 | 682.3693 | 2261.8537
2015-08-03 08:30 | 931 | 619 | 2020 | 7 | 0 | 327257 | 3131 | dr | 2 | 0 |  | 24.9167 | 896.7492 | 596.2274 | 1945.6856
2015-08-04 08:00 | 1021 | 558 | 2190 | 6 | 0 | 328357 | 3137 | dr | 3 | 0 | time estimated, not on record sheet | 23.5 | 1042.7234 | 569.8723 | 2236.5957
2015-08-05 09:00 | 1107 | 728 | 2393 | 5 | 0 | 329457 | 3145 | dr | 2 | 0 | time estimated, not on record sheet | 25 | 1062.72 | 698.88 | 2297.28
2015-08-06 08:14 | 994 | 671 | 2345 | 7 | 0 | 330457 | 3152 | zn | 3 | 0 |  | 23.2333 | 1026.8006 | 693.142 | 2422.3816
2015-08-07 08:25 | 889 | 762 | 1958 | 6 | 0 | 331357 | 3158 | zn | 2 | 0 |  | 24.1833 | 882.2605 | 756.2233 | 1943.1564
2015-08-08 09:00 | 1012 | 627 | 2157 | 7 | 0 |  |  | dk | 2 | 0 |  | 24.5833 | 987.9864 | 612.122 | 2105.8169
2015-08-09 08:40 | 1112 | 671 | 2366 | 7 | 0 | 333557 | 3171 | zn | 2 | 0 |  | 23.6667 | 1127.662 | 680.4507 | 2399.3239
2015-08-10 08:14 | 884 | 682 | 1905 | 6 | 0 | 334357 | 3177 | zn | 2 | 0 |  | 23.5667 | 900.2546 | 694.5403 | 1940.0283
2015-08-11 08:19 | 1092 | 701 | 2350 | 7 | 0 | 335457 | 3184 | zn | 3 | 0 |  | 24.0833 | 1088.2215 | 698.5744 | 2341.8685
2015-08-12 07:45 | 1176 | 740 | 2515 | 7 | 0 | 336857 | 3192 | zn | 2 | 0 |  | 23.4333 | 1204.4381 | 757.8947 | 2575.8179
2015-08-14 09:20 | 2331 | 1448 | 5360 | 15 | 0 | 339057 | 3207 | zn | 5 | 0 |  | 49.5833 | 1128.2824 | 700.8807 | 2594.4202
2015-08-15 08:10 | 1138 | 637 | 2535 | 7 | 0 | 340257 | 3215 | bb | 2 | 0 |  | 22.8333 | 1196.146 | 669.5474 | 2664.5255
2015-08-16 08:20 | 1405 | 619 | 3090 | 8 | 0 | 341657 | 3224 | bb | 3 | 0 |  | 24.1667 | 1395.3103 | 614.731 | 3068.6897
2015-08-17 08:24 | 1222 | 565 | 3102 | 8 | 0 | 342857 | 3233 | zn | 3 | 0 |  | 24.0667 | 1218.615 | 563.4349 | 3093.4072
2015-08-18 08:18 | 1439 | 725 | 3244 | 9 | 0 | 344357 | 3243 | zn | 4 | 0 |  | 23.9 | 1445.0209 | 728.0335 | 3257.5732
2015-08-19 08:10 | 1575 | 643 | 3346 | 8 | 0 | 345957 | 3253 | bb | 3 | 0 |  | 23.8667 | 1583.7989 | 646.5922 | 3364.6927
2015-08-20 08:00 | 1436 | 580 | 3038 | 8 | 0 | 347457 | 3262 | zn | 3 | 0 |  | 23.8333 | 1446.042 | 584.0559 | 3059.2448
2015-08-21 09:07 | 1536 | 626 | 3658 | 9 | 0 | 348957 | 3271 | zn | 4 | 0 |  | 25.1167 | 1467.7107 | 598.1685 | 3495.3683
2015-08-22 08:09 | 1426 | 596 | 3041 | 8 | 0 | 350457 | 3280 | zn | 2 | 0 |  | 23.0333 | 1485.8466 | 621.013 | 3168.6252
2015-08-23 08:10 | 1375 | 604 | 3064 | 8 | 0 | 351757 | 3290 | zn | 3 | 0 |  | 24.0167 | 1374.0458 | 603.5808 | 3061.8737
2015-08-24 09:03 | 1475 | 602 | 3252 | 9 | 0 | 353257 | 3299 | zn | 3 | 0 |  | 24.8833 | 1422.639 | 580.6296 | 3136.5573
2015-08-25 07:57 | 1386 | 606 | 2959 | 8 | 0 | 354657 | 3308 | zn | 3 | 0 |  | 22.9 | 1452.5764 | 635.1092 | 3101.1354
2015-08-26 08:00 | 1567 | 654 | 3351 | 8 | 0 | 356257 | 3318 | zn | 3 | 0 |  | 24.05 | 1563.7422 | 652.6403 | 3344.0333
2015-08-27 07:56 | 1441 | 584 | 3082 | 8 | 0 | 357757 | 3327 | zn | 2 | 0 |  | 23.9333 | 1445.0139 | 585.6267 | 3090.585
2015-08-28 07:38 | 1414 | 593 | 3041 | 8 | 0 | 359157 | 3336 | zn | 2 | 0 |  | 23.7 | 1431.8987 | 600.5063 | 3079.4937
2015-08-29 07:56 | 595 | 665 | 1272 | 4 | 4 | 359757 | 3340 | dk | 1 | 0 | genset off during night | 24.3 | 587.6543 | 656.7901 | 1256.2963
2015-08-30 08:25 | 1283 | 626 | 3548 | 8 | 1 | 361057 | 3350 | zn | 3 | 0 |  | 24.4833 | 1257.6719 | 613.6419 | 3477.9578
2015-08-31 08:10 | 1804 | 633 | 3768 | 8 | 0 | 362157 | 3361 | zn | 3 | 0 |  | 23.75 | 1822.9895 | 639.6632 | 3807.6632
2015-09-01 08:14 | 1221 | 606 | 4482 | 9 | 0 | 363457 | 3374 | zn | 4 | 0 |  | 24.0667 | 1217.6177 | 604.3213 | 4469.5845
2015-09-02 10:34 | 2008 | 678 | 5206 | 9 | 0 | 365457 | 3389 | bc | 4 | 0 |  | 26.3333 | 1830.0759 | 617.9241 | 4744.7089
2015-09-03 07:57 | 1519 | 455 | 4043 | 7 | 0 | 366957 | 3041 | zn | 4 | 0 |  | 21.3833 | 1704.8792 | 510.6781 | 4537.7397
2015-09-04 09:13 | 993 | 685 | 2509 | 4 | 1 | 367957 | 3408 | bc | 2 | 0 | genset off during night | 25.2667 | 943.219 | 650.6596 | 2383.219
2015-09-05 07:40 | 2828 | 561 | 727 | 4 | 1 | 368757 | 3416 | zn | 3 | 0 | genset off during night | 22.45 | 3023.2517 | 599.7327 | 777.1938
2015-09-06 08:17 | 1338 | 664 | 4989 | 7 | 1 | 370157 | 3430 | zn | 3 | 0 | genset off during night | 24.6167 | 1304.4821 | 647.3663 | 4864.0217
2015-09-07 09:55 | 1625 | 680 | 5865 | 8 | 2 | 371757 | 3446 | zn | 5 | 0 |  | 25.6333 | 1521.4564 | 636.671 | 5491.2874
2015-09-08 07:56 | 1337 | 488 | 5075 | 5 | 9 | 373057 | 3461 | zn | 4 | 0 | genset down briefly | 22.0167 | 1457.4413 | 531.9606 | 5532.1726
2015-09-09 08:00 | 1401 | 599 | 5398 | 5 | 24 | 374557 | 3476 | zn | 5 | 0 | genset problems | 24.0667 | 1397.1191 | 597.3407 | 5383.0471
2015-09-11 09:05 | 1668 | 1292 | 5817 | 6 | 60 | 376257 | 3492 | bc | 10 | 0 | genset problems | 49.0833 | 815.5925 | 631.7419 | 2844.3056
2015-09-13 09:30 | 812 | 1218 | 3078 | 3 | 77 | 377057 | 3501 | dk | 2 | 0 | genset offline | 48.4167 | 402.506 | 603.759 | 1525.7556
2015-09-14 08:08 | 0 | 498 | 0 | 0 | 39 | 377057 | 3501 | zn | 0 | 0 | genset offline | 22.6333 | 0 | 528.0707 | 0
2015-09-15 08:14 | 0 | 630 | 0 | 0 | 43 | 377057 | 3501 | zn | 0 | 0 | genset offline | 24.1 | 0 | 627.3859 | 0
2015-09-16 08:16 | 0 | 663 | 0 | 0 | 42 | 377057 | 3501 | zn | 0 | 0 | genset offline | 24.0333 | 0 | 662.0804 | 0
2015-09-17 08:00 | 0 | 612 | 0 | 0 | 40 | 377057 | 3501 | zn | 0 | 0 | genset offline | 23.7333 | 0 | 618.8764 | 0
2015-09-18 08:05 | 0 | 690 | 0 | 0 | 39 | 377057 | 3501 | zn | 0 | 0 | restarted genset 15:30, manually emptied flare water trap | 24.0833 | 0 | 687.6125 | 0
2015-09-19 08:40 | 811 | 658 | 3105 | 6 | 11 | 377857 | 3509 | zn | 2 | 0 |  | 24.5833 | 791.7559 | 642.3864 | 3031.322
2015-09-20 09:07 | 1201 | 632 | 4479 | 9 | 0 | 379057 | 3522 | zn | 2 | 0 |  | 24.45 | 1178.8957 | 620.3681 | 4396.5644
2015-09-21 09:03 | 1315 | 639 | 4825 | 7 | 0 | 380357 | 3536 | bc | 2 | 0 |  | 23.9333 | 1318.663 | 640.7799 | 4838.4401
2015-09-22 07:57 | 1301 | 609 | 4812 | 7 | 0 | 381757 | 3550 | zn | 2 | 0 |  | 22.9 | 1363.4934 | 638.2533 | 5043.1441
2015-09-23 08:25 | 1356 | 668 | 4982 | 8 | 0 | 383057 | 3564 | bc | 2 | 0 |  | 24.4667 | 1330.1362 | 655.2589 | 4886.9755
2015-09-24 08:05 | 1418 | 588 | 5260 | 7 | 0 | 384557 | 3579 | zn | 1 | 0 |  | 23.6667 | 1437.9718 | 596.2817 | 5334.0845
2015-09-25 09:28 | 1570 | 635 | 5603 | 7 | 0 | 386157 | 3595 | zn | 3 | 0 |  | 25.3833 | 1484.4386 | 600.394 | 5297.6494
2015-09-26 08:24 | 1473 | 522 | 5374 | 7 | 0 | 387657 | 3610 | dk | 3 | 0 |  | 22.9333 | 1541.5116 | 546.2791 | 5623.9535
2015-09-27 10:25 | 1804 | 647 | 6743 | 7 | 0 | 389457 | 3629 | dk | 3 | 0 |  | 26.0167 | 1664.164 | 596.8482 | 6220.3203
2015-09-28 09:42 | 1465 | 498 | 5380 | 8 | 5 | 390957 | 3644 | bc | 3 | 0 |  | 23.2833 | 1510.0931 | 513.3286 | 5545.5977
2015-09-29 07:55 | 1361 | 513 | 5265 | 7 | 0 | 392357 | 3659 | zn | 3 | 0 |  | 22.2167 | 1470.2476 | 554.1785 | 5687.6219
2015-09-30 09:20 | 1646 | 728 | 6502 | 7 | 0 | 393957 | 3677 | bc | 4 | 0 |  | 25.4167 | 1554.2557 | 687.423 | 6139.5934
2015-10-01 08:05 | 735 | 609 | 2804 | 3 | 22 | 394757 | 3685 | zn | 1 | 0 |  | 22.75 | 775.3846 | 642.4615 | 2958.0659
2015-10-02 09:39 | 2009 | 707 | 6640 | 6 | 0 | 396757 | 3704 | zn | 2 | 0 |  | 25.5667 | 1885.8931 | 663.6767 | 6233.116
2015-10-03 09:20 | 1575 | 608 | 5951 | 6 | 0 | 398357 | 3720 | zn | 2 | 0 |  | 23.6833 | 1596.0591 | 616.1295 | 6030.57
2015-10-04 08:02 | 1427 | 575 | 5452 | 7 | 0 | 399857 | 3736 | zn | 2 | 1 |  | 22.7 | 1508.7225 | 607.9295 | 5764.2291
2015-10-05 08:30 | 1798 | 659 | 6315 | 7 | 0 | 401657 | 3753 | zn | 3 | 0 |  | 24.4667 | 1763.7057 | 646.4305 | 6194.5504
2015-10-06 08:15 | 1873 | 581 | 5684 | 7 | 0 | 403557 | 3769 | bc | 4 | 0 |  | 23.75 | 1892.7158 | 587.1158 | 5743.8316
2015-10-07 10:25 | 1991 | 686 | 6063 | 8 | 0 | 405557 | 3786 | bc | 3 | 0 |  | 26.1667 | 1826.1401 | 629.1975 | 5560.9682
2015-10-08 07:53 | 1282 | 484 | 4331 | 7 | 0 | 406857 | 3799 | zn | 2 | 0 |  | 21.4667 | 1433.2919 | 541.118 | 4842.1118
2015-10-09 08:38 | 1523 | 633 | 4854 | 8 | 0 | 408457 | 3813 | bc | 3 | 0 |  | 24.75 | 1476.8485 | 613.8182 | 4706.9091
2015-10-10 09:38 | 1437 | 683 | 4080 | 8 | 0 | 409857 | 3825 | dk | 1 | 0 |  | 25 | 1379.52 | 655.68 | 3916.8
2015-10-11 09:54 | 923 | 574 | 3442 | 7 | 0 | 410857 | 3835 | dk | 1 | 0 |  | 24.2667 | 912.8571 | 567.6923 | 3404.1758
2015-10-12 08:15 | 916 | 526 | 2843 | 7 | 0 | 411757 | 3843 | zn | 2 | 1 |  | 22.35 | 983.6242 | 564.8322 | 3052.8859
2015-10-13 08:00 | 1418 | 593 | 3317 | 7 | 0 | 413257 | 3853 | zn | 2 | 0 |  | 23.75 | 1432.9263 | 599.2421 | 3351.9158
2015-10-14 08:19 | 1477 | 611 | 3166 | 8 | 0 | 414757 | 3862 | zn | 2 | 0 |  | 24.3167 | 1457.7656 | 603.0432 | 3124.7704
2015-10-15 08:18 | 1316 | 583 | 2961 | 7 | 0 | 416057 | 3871 | zn | 1 | 0 |  | 23.9833 | 1316.9145 | 583.4051 | 2963.0577
2015-10-16 09:00 | 1323 | 601 | 2958 | 7 | 0 | 417457 | 3879 | zn | 2 | 0 |  | 24.7 | 1285.5061 | 583.9676 | 2874.17
2015-10-17 08:10 | 1370 | 556 | 2979 | 8 | 0 | 418757 | 3888 | zn | 1 | 0 |  | 23.1667 | 1419.2806 | 576 | 3086.1583
2015-10-18 09:23 | 1005 | 718 | 2920 | 6 | 0 | 419857 | 3897 | zn | 1 | 0 |  | 25.2167 | 956.5102 | 683.3576 | 2779.1143
2015-10-19 09:18 | 786 | 583 | 3034 | 7 | 0 | 420657 | 3905 | bc | 0 | 1 |  | 23.9167 | 788.7387 | 585.0314 | 3044.5714
2015-10-20 07:55 | 946 | 623 | 3219 | 7 | 0 | 421557 | 3915 | zn | 1 | 0 |  | 22.6167 | 1003.8615 | 661.1054 | 3415.888
2015-10-21 08:15 | 1331 | 643 | 3236 | 8 | 0 | 422957 | 3924 | zn | 2 | 0 |  | 24.3333 | 1312.7671 | 634.1918 | 3191.6712
2015-10-22 07:29 | 1286 | 608 | 3267 | 7 | 0 | 424257 | 3934 | dk | 2 | 0 |  | 23.2333 | 1328.4362 | 628.0631 | 3374.8063
2015-10-23 10:30 | 1399 | 791 | 3385 | 8 | 0 | 425657 | 3944 | bc | 1 | 0 |  | 27.0167 | 1242.7884 | 702.6774 | 3007.0327
2015-10-24 08:07 | 1093 | 508 | 2665 | 6 | 0 | 426857 | 3952 | dk | 1 | 0 |  | 21.6167 | 1213.5081 | 564.0093 | 2958.8281
2015-10-25 07:58 | 1328 | 558 | 3317 | 8 | 0 | 428057 | 3961 | dk | 1 | 0 |  | 23.85 | 1336.3522 | 561.5094 | 3337.8616
2015-10-26 09:20 | 1189 | 607 | 3323 | 7 | 0 | 429257 | 3971 | bc | 1 | 1 |  | 25.3667 | 1124.9409 | 574.297 | 3143.9685
2015-10-27 08:48 | 1219 | 625 | 2926 | 7 | 0 | 430997 | 3980 | zn | 1 | 0 |  | 23.4667 | 1246.7045 | 639.2045 | 2992.5
2015-10-28 08:03 | 1487 | 564 | 3466 | 7 | 0 | 432057 | 3990 | zn | 2 | 0 |  | 23.25 | 1534.9677 | 582.1935 | 3577.8065
2015-10-29 08:04 | 1729 | 647 | 3762 | 8 | 2 | 433757 | 4001 | zn | 0 | 0 | power outage wed. afternoon prevented flare from auto starting, flare burned some until genset manually restarted | 24.0167 | 1727.8001 | 646.551 | 3759.3893
2015-10-30 08:48 | 1851 | 600 | 3911 | 8 | 0 | 435657 | 4012 | zn | 3 | 0 |  | 24.7333 | 1796.1186 | 582.2102 | 3795.0404
2015-10-31 09:15 | 2094 | 597 | 4561 | 9 | 0 | 437757 | 4025 | bc | 1 | 0 |  | 24.45 | 2055.4601 | 586.0123 | 4477.0552
2015-11-01 07:10 | 1545 | 535 | 4580 | 7 | 0 | 439357 | 4038 | bc | 2 | 0 |  | 21.9167 | 1691.8631 | 585.8555 | 5015.3612
2015-11-02 07:10 | 2653 | 562 | 4320 | 8 | 0 | 440457 | 4051 | bc | 1 | 0 |  | 24 | 2653 | 562 | 4320
2015-11-03 08:02 | 1386 | 601 | 5205 | 8 | 0 | 441857 | 4065 | zn | 2 | 0 |  | 24.8667 | 1337.6944 | 580.0536 | 5023.5925
2015-11-04 06:30 | 1178 | 532 | 4567 | 7 | 0 | 443057 | 4078 | bc | 2 | 1 |  | 22.4667 | 1258.3976 | 568.3086 | 4878.6944
2015-11-05 09:00 | 1413 | 691 | 5519 | 8 | 0 | 444557 | 4094 | zn | 3 | 0 |  | 26.5 | 1279.6981 | 625.8113 | 4998.3396
2015-11-06 07:29 | 1759 | 518 | 5027 | 7 | 0 | 446257 | 4108 | zn | 3 | 0 |  | 22.4833 | 1877.6575 | 552.9429 | 5366.1082
2015-11-07 09:35 | 2257 | 655 | 5583 | 9 | 0 | 448457 | 4123 | zn | 3 | 0 |  | 26.1 | 2075.4023 | 602.2989 | 5133.7931
2015-11-08 08:05 | 1330 | 544 | 4185 | 8 | 0 | 449957 | 4136 | zn | 2 | 0 |  | 22.5 | 1418.6667 | 580.2667 | 4464
2015-11-09 08:21 | 1202 | 546 | 4516 | 7 | 0 | 451157 | 4149 | bc | 1 | 0 |  | 24.2667 | 1188.7912 | 540 | 4466.3736
2015-11-10 07:52 | 1103 | 516 | 3973 | 7 | 10 | 452257 | 4161 | zn | 1 | 1 | genset off Monday morning for maintenance | 23.5167 | 1125.6697 | 526.6052 | 4054.6563
2015-11-11 08:36 | 1786 | 664 | 5081 | 8 | 0 | 454057 | 4175 | bc | 2 | 0 |  | 24.7333 | 1733.0458 | 644.3127 | 4930.3504
2015-11-12 07:42 | 1229 | 551 | 4314 | 7 | 0 | 455357 | 4188 | zn | 2 | 0 |  | 23.1 | 1276.8831 | 572.4675 | 4482.0779
2015-11-13 08:25 | 1309 | 582 | 4669 | 9 | 0 | 456657 | 4201 | bc | 3 | 0 |  | 24.7167 | 1271.0452 | 565.1247 | 4533.621
2015-11-14 07:45 | 1482 | 536 | 4032 | 7 | 0 | 458157 | 4213 | bc | 1 | 0 |  | 23.3333 | 1524.3429 | 551.3143 | 4147.2
2015-11-15 07:45 | 1082 | 613 | 4276 | 8 | 0 | 459257 | 4225 | bc | 1 | 1 |  | 24 | 1082 | 613 | 4276
2015-11-16 07:56 | 1180 | 553 | 4642 | 7 | 0 | 460457 | 4238 | zn | 1 | 0 |  | 24.1833 | 1171.0544 | 548.8077 | 4606.8091
2015-11-17 07:24 | 1287 | 617 | 5008 | 8 | 0 | 461757 | 4252 | dk | 2 | 0 |  | 23.4667 | 1316.25 | 631.0227 | 5121.8182
2015-11-18 08:14 | 1414 | 610 | 5571 | 7 | 0 | 463157 | 4268 | bc | 1 | 0 |  | 24.8333 | 1366.5503 | 589.5302 | 5384.0537
2015-11-19 08:40 | 1223 | 608 | 4791 | 8 | 0 | 464457 | 4282 | zn | 1 | 0 |  | 24.4333 | 1201.3097 | 597.2169 | 4706.03
2015-11-20 07:40 | 1149 | 530 | 4462 | 7 | 0 | 465557 | 4295 | dk | 1 | 1 |  | 23 | 1198.9565 | 553.0435 | 4656
2015-11-21 08:15 | 1243 | 605 | 4806 | 7 | 0 | 466857 | 4308 | zn | 1 | 0 |  | 24.5833 | 1213.5051 | 590.6441 | 4691.9593
2015-11-22 09:55 | 1131 | 581 | 4297 | 9 | 0 | 468057 | 4321 | zn | 1 | 0 |  | 25.6667 | 1057.5584 | 543.2727 | 4017.974
2015-11-23 08:27 | 924 | 563 | 3558 | 6 | 0 | 468957 | 4331 | bc | 0 | 0 |  | 22.5333 | 984.142 | 599.645 | 3789.5858
2015-11-24 08:35 | 957 | 608 | 3738 | 8 | 0 | 469957 | 4342 | zn | 1 | 0 |  | 24.1333 | 951.7127 | 604.6409 | 3717.3481
2015-11-25 08:29 | 1111 | 585 | 4321 | 8 | 0 | 471057 | 4354 | bc | 0 | 0 |  | 23.9 | 1115.6485 | 587.4477 | 4339.0795
2015-11-26 07:52 | 1548 | 576 | 4886 | 7 | 0 | 472657 | 4368 | dk | 2 | 2 |  | 23.3833 | 1588.8239 | 591.1903 | 5014.8539
2015-11-27 07:40 | 1222 | 556 | 4821 | 8 | 0 | 473857 | 4382 | bc | 1 | 0 |  | 23.8 | 1232.2689 | 560.6723 | 4861.5126
2015-11-28 08:15 | 716 | 674 | 2331 | 4 | 24 | 474557 | 4389 | dk | 1 | 0 |  | 24.5833 | 699.0102 | 658.0068 | 2275.6881
2015-11-29 07:55 | 1227 | 585 | 4523 | 7 | 0 | 475857 | 4401 | dk | 1 | 0 |  | 23.6667 | 1244.2817 | 593.2394 | 4586.7042
2015-11-30 07:30 | 1576 | 620 | 5043 | 6 | 1 | 477457 | 4416 | bc | 0 | 0 |  | 23.5833 | 1603.8445 | 630.9541 | 5132.0989
2015-12-01 07:50 | 1871 | 696 | 6030 | 6 | 0 | 479357 | 4433 | zn | 0 | 0 | manually emptied water trap 2 | 24.3333 | 1845.3699 | 686.4658 | 5947.3973
2015-12-02 07:40 | 1321 | 766 | 5201 | 8 | 0 | 482157 | 4463 | zn | 1 | 0 |  | 23.8333 | 1330.2378 | 771.3566 | 5237.3706
2015-12-03 08:20 | 1321 | 766 | 5201 | 8 | 0 | 482157 | 4463 | zn | 1 | 0 |  | 24.6667 | 1285.2973 | 745.2973 | 5060.4324
2015-12-04 07:40 | 1189 | 585 | 4529 | 8 | 0 | 483357 | 4476 | bc | 1 | 1 |  | 23.3333 | 1222.9714 | 601.7143 | 4658.4
2015-12-05 09:05 | 1416 | 646 | 5394 | 8 | 0 | 484857 | 4492 | zn | 2 | 0 |  | 25.4167 | 1337.0754 | 609.9934 | 5093.3508
2015-12-06 08:05 | 1287 | 543 | 5085 | 7 | 0 | 486157 | 4506 | zn | 2 | 0 |  | 23 | 1342.9565 | 566.6087 | 5306.087
2015-12-07 07:40 | 1270 | 555 | 4940 | 7 | 0 | 487457 | 4520 | bc | 1 | 0 | hydrolyzer levels graph shows feeding not going correctly on dec 7,8,9 | 23.5833 | 1292.4382 | 564.8057 | 5027.2792
2015-12-08 08:07 | 1100 | 715 | 4196 | 7 | 0 | 488557 | 4532 | zn | 1 | 0 |  | 24.45 | 1079.7546 | 701.8405 | 4118.773
2015-12-09 09:41 | 1535 | 664 | 4435 | 8 | 0 | 490057 | 4545 | bc | 1 | 0 | manually emptied water trap 2 | 25.5667 | 1440.9387 | 623.3116 | 4163.2334
2015-12-10 08:55 | 1612 | 466 | 3423 | 8 | 0 | 491857 | 4556 | zn | 2 | 0 |  | 23.2333 | 1665.1937 | 481.3773 | 3535.9541
2015-12-11 09:02 | 2625 | 483 | 5597 | 8 | 0 | 494357 | 4571 | bc | 4 | 0 |  | 24.1167 | 2612.3013 | 480.6634 | 5569.924
2015-12-12 07:53 | 2850 | 452 | 6129 | 7 | 10 | 497257 | 4588 | bc | 5 | 0 |  | 22.85 | 2993.4354 | 474.7484 | 6437.4617
2015-12-13 07:35 | 2382 | 460 | 7060 | 5 | 0 | 499657 | 4608 | bc | 5 | 0 |  | 23.7 | 2412.1519 | 465.8228 | 7149.3671
2015-12-14 07:35 | 1749 | 537 | 7026 | 5 | 0 | 501457 | 4627 | bc | 4 | 0 |  | 24 | 1749 | 537 | 7026
2015-12-15 08:05 | 1933 | 600 | 7720 | 4 | 0 | 503457 | 4648 | zn | 4 | 0 |  | 24.5 | 1893.551 | 587.7551 | 7562.449
pH wanted in digester = 6.8 - 8.0
hydrolyzer needs to be above 5
balloon volume
400 m3
Note on E168: Nuite, Zyla: 1/22,23,24 flare and genset being cycled manually for troubleshooting and testing. Genset setpoints moved to 70, 20
Note on F194: Nuite, Zyla: flare water trap pump ran 0 times. Frozen? Flare stopped working early morning, gas vented to atmosphere from digester and hydrolyzer
Note on F203: Nuite, Zyla: genset shutdown, high H2S

## biogas
datetime | CH4 % | meter | H2S ppm | meter
2014-03-28 08:20 | 55.3 | F | 110 | F | jp
2014-06-06 14:13 | 24 | F
2014-06-07 07:15 | 24 | F
2014-06-09 08:45 | 25 | F
2014-06-11 08:55 | 26 | F
2014-06-12 11:30 | 28 | F | 955 | F
2014-06-13 10:00 | 29 | F | 910 | F
2014-06-16 10:00 | 40 | F | 880 | F
2014-06-17 09:30 | 46 | F | 795 | F
2014-06-18 09:00 | 57 | F | 675 | F
2014-06-19 09:30 | 66 | F | 430 | F
2014-06-20 08:40 | 70 | F | 316 | F
2014-06-23 10:30 | 64 | F | 415 | F
2014-06-24 08:30 | 63 | F | 415 | F
2014-06-25 07:30 | 61 | F | 350 | F
2014-06-25 13:00 | 60 | F | 285 | F
2014-06-30 10:30 | 57 | F | 180 | F
2014-07-01 07:30 | 57 | F | 190 | F
2014-07-02 14:30 | 57 | F | 230 | F
2014-07-03 07:30 | 60 | F | 180 | F
2014-07-07 08:30 | 64 | F | 140 | F
2014-07-08 07:30 | 55 | F | 60 | F
2014-07-10 07:30 | 53 | F | 55 | F
2014-07-11 09:00 | 54 | F | 5 | F
2014-07-14 09:00 | 61 | F | 80 | F
2014-07-15 07:30 | 64 | F | 68 | F
2014-07-16 07:00 | 63 | F | 88 | F
2014-07-21 09:30 | 61 | F | 35 | F
2014-07-22 08:00 | 63 | F | 75 | F
2014-07-23 08:00 | 62 | F | 8 | F
2014-07-24 07:30 | 61 | F | 13 | F
2014-07-28 08:00 | 60 | F | 63 | F
2014-07-29 07:30 | 60 | F | 33 | F
2014-07-30 | 60 | F
2014-08-01 14:00 | 59 | F | 5 | F
2014-08-04 | 59 | F | 52 | F
2014-08-05 10:00 | 60 | F
2014-08-06 09:30 | 60 | F | 0 | F
2014-08-07 15:00 | 59 | F | 0 | F
2014-08-08 09:00 | 58 | F | 15 | F
2014-08-12 10:00 | 64 | F | 228 | F
2014-08-13 07:30 | 64 | F | 60 | F
2014-08-14 13:30 | 63 | F | 44 | F
2014-08-15 15:45 | 63 | F | 1 | F
2014-08-19 14:45 | 65 | F | 0 | F
2014-08-20 15:45 | 63 | F | 0 | F
2014-08-21 | 62 | F | 10 | F
2014-08-22 10:37 | 61 | F | 0 | F
2014-08-25 07:00 | 63 | F | 20 | F
2014-08-26 08:00 | 64 | F | 5 | F
2014-08-27 08:30 | 64 | F | 122 | F
2014-08-28 07:30 | 64 | F | 141 | F
2014-08-29 07:30 | 63 | F | 9 | F
2014-09-02 | 65 | F | 72 | F
2014-09-03 | 64.5 | F | 42 | F
2014-09-04 10:30 | 64 | F | 14 | F
2014-09-05 08:30 | 63 | F | 11 | F
2014-09-08 07:30 | 60 | F | 9 | F
2014-09-09 10:30 | 60 | F | 17 | F
2014-09-10 07:00 | 60 | F | 12 | F
2014-09-11 07:00 | 60 | F | 8 | F
2014-09-12 07:00 | 58 | F | 6 | F
2014-09-15 09:00 | 60 | F | 11 | F
2014-09-16 09:00 | 61 | F | 18 | F
2014-09-17 09:00 | 60 | F | 13 | F
2014-09-18 09:00 | 60 | F | 16 | F
2014-09-19 13:00 | 60 | F | 10 | F
2014-09-22 07:30 | 60 | F | 19 | F
2014-09-23 10:00 | 58 | F | 9 | F
2014-09-24 09:00 | 58 | F | 13 | F
2014-09-25 15:00 | 59 | F | 83 | F
2014-09-26 11:30 | 61 | F | 28 | F
2014-09-27 17:00 | 56 | F | 180 | F
2014-09-28 10:30 | 58.8 | F | 334 | F
2014-09-29 08:30 | 61 | F | 378 | F
2014-09-30 07:30 | 62 | F | 400 | F
2014-10-01 08:00 | 65 | F | 850 | F
2014-10-02 09:00 | 67 | F | 800 | F
2014-10-02 15:00 |  |  | 450 | F
2014-10-03 09:00 | 68 | F | 520 | F
2014-10-05 18:37 | 68.6 | F | 290 | F
2014-10-06 | 60 | F | 300 | F
2014-10-07 10:00 |  |  | 338 | F
2014-10-08 08:00 |  |  | 310 | F
2014-10-09 09:30 | 67.6 | F | 152 | F
2014-10-10 10:00 | 66.6 | F | 3 | F
2014-10-11 16:00 | 65.2 | F | 9 | F
2014-10-12 17:45 | 65.8 | F | 77 | F
2014-10-13 09:30 | 65 | F | 141 | F
2014-10-14 09:00 | 62.3 | F | 215 | F
2014-10-15 08:24 | 61.4 | F | 380 | F
2014-10-16 08:30 | 60 | F | 560 | F
2014-10-17 08:10 | 59.6 | F | 490 | F
2014-10-18 13:15 | 55.4 | F | 615 | F
2014-10-19 18:42 | 58.3 | F | 525 | F
2014-10-20 08:30 | 58 | F | 645 | F
2014-10-21 08:30 | 58.5 | F | 580 | F
2014-10-22 08:00 | 55.1 | F | 565 | F
2014-10-23 08:00 | 56.1 | F | 390 | F
2014-10-23 16:50 | 40 | F | 180 | F
2014-10-24 08:30 | 67.8 | w | 140 | F
2014-10-25 16:30 | 60.1 | w | 65 | F
2014-10-26 17:30 | 69.5 | w | 145 | F
2014-10-27 07:00 | 69.3 | w | 125 | F
2014-10-28 08:00 | 68 | w | 20 | F
2014-10-29 11:30 | 66.4 | w | 35 | F
2014-10-30 08:30 | 64.5 | w | 20 | F
2014-10-31 08:00 | 65.4 | w | 20 | F
2014-11-03 07:30 | 64 | w | 5 | F
2014-11-04 08:00 | 64 | w | 15 | F
2014-11-05 08:30 | 64.5 | w | 10 | F
2014-11-06 07:30 | 65.2 | w | 10 | F
2014-11-07 07:30 | 65.3 | w | 10 | F
2014-11-10 07:55 | 69.7 | w | 5 | F
2014-11-11 08:30 | 69.3 | w | 5 | F
2014-11-12 08:15 | 69.3 | w | 5 | F
2014-11-13 07:15 | 67.5 | w | 5 | F
2014-11-14 08:15 | 67.2 | w | 5 | F
2014-11-17 08:30 | 67 | w | 5 | F
2014-11-18 08:20 | 66.5 | w | 5 | F
2014-11-19 08:20 | 65.9 | w | 5 | F
2014-11-20 07:30 | 66.1 | w | 0 | F
2014-11-21 09:20 | 65 | w | 0 | F
2014-11-24 08:40 | 67.2 | w | 5 | F
2014-11-25 08:30 | 66.7 | w | 5 | F
2014-11-26 09:45 | 67.6 | w | 10 | F
2014-11-28 08:30 | 66.9 | w | 10 | F
2014-12-01 08:00 | 67.3 | w | 15 | F
2014-12-02 08:00 | 67.4 | w | 5 | F
2014-12-03 09:50 | 67 | w | 5 | F
2014-12-04 08:00 | 64.6 | w | 5 | F
2014-12-05 09:15 | 62.2 | w | 0 | F
2014-12-08 11:30 | 66.3 | w
2014-12-09 09:30 | 65.4 | w | 0 | F
2014-12-10 09:30 | 53.2 | F | 0 | F |  | wall meter down since power outage
2014-12-11 08:45 | 52.7 | F | 0 | F
2014-12-12 08:15 | 56.1 | F | 50 | F
2014-12-14 09:00 | 60.4 | F | 35 | F
2014-12-17 08:30 | 58.5 | F | 10 | F
2014-12-18 08:00 | 57.9 | F | 10 | F
2014-12-19 10:00 | 55.7 | F | 10 | F
2014-12-22 08:45 | 57.3 | F | 60 | F
2014-12-23 08:00 | 52.2 | F | 40 | F
2014-12-24 09:50 | 54.4 | F | 30 | F
2014-12-25 07:50 | 55.2 | F | 50 | F
2014-12-26 08:00 | 57 | F | 40 | F
2014-12-29 08:30 | 58.2 | F | 115 | F
2014-12-30 07:30 | 58.4 | F | 105 | F
2014-12-31 08:00 | 56.3 | F | 75 | F
2015-01-02 07:45 | 55.3 | F | 115 | F
2015-01-05 08:00 | 55.5 | F | 60 | F
2015-01-06 08:15 | 54.3 | F | 180 | F
2015-01-07 09:00 | 53.6 | F | 225 | F
2015-01-08 07:50 | 55.3 | F | 235 | F
2015-01-09 08:40 | 57 | F | 225 | F
2015-01-10 09:00 | 56.8 | F | 220 | F
2015-01-11 11:20 | 56.7 | F | 235 | F
2015-01-12 07:39 | 57.8 | F | 245 | F
2015-01-13 08:00 | 56.4 | F | 205 | F
2015-01-14 08:50 | 56.3 | F | 160 | F
2015-01-15 07:30 | 55.2 | F | 180 | F
2015-01-16 09:00 | 56.6 | F | 175 | F
2015-01-17 08:20 | 59.9 | F | 155 | F
2015-01-18 14:00 | 58.5 | F | 240 | F
2015-01-20 09:13 | 55.4 | F | 50 | F
2015-01-22 07:45 | 54.5 | F | 120 | F
2015-01-23 08:15 | 56.9 | F | 120 | F
2015-01-24 08:50 | 56 | F | 100 | F
2015-01-25 08:25 | 57.2 | F | 95 | F
2015-01-26 07:50 | 59.2 | F | 150 | F
2015-01-27 09:30 | 57.2 | F | 155 | F
2015-01-28 09:30 | 57.1 | F | 180 | F
2015-01-29 08:00 | 57.7 | F | 205 | F
2015-01-30 08:45 | 56.4 | F | 185 | F
2015-01-31 11:00 | 55.2 | F | 150 | F
2015-02-01 08:00 | 55.7 | F | 155 | F | pf
2015-02-02 08:35 | 58.4 | F | 130 | F | zn
2015-02-03 09:00 | 55.4 | F | 110 | F | zn
2015-02-04 10:20 | 58.1 | F | 125 | F | zn
2015-02-05 10:20 | 59.9 | F | 70 | F | pf
2015-02-06 08:40 | 57.2 | F | 100 | F | zn
2015-02-07 10:00 | 55.7 | F | 75 | F | zn
2015-02-08 08:50 | 54.2 | F | 95 | F | zn
2015-02-09 14:25 | 55.8 | F | 105 | F | zn
2015-02-10 08:15 | 54.9 | F | 170 | F | zn
2015-02-11 09:25 | 54.8 | F | 180 | F | jp
2015-02-12 07:50 | 53.9 | F | 220 | F | pf
2015-02-13 07:53 | 49.3 | F | 220 | F | zn
2015-02-14 10:50 | 49.3 | F | 340 | F | jp
2015-02-15 12:10 | 55.3 | F | 195 | F | jp
2015-02-16 09:30 | 56.5 | F | 95 | F | jp
2015-02-17 08:30 | 56.6 | F | 245 | F | zn
2015-02-18 10:00 | 52.9 | F | 260 | F | zn
2015-02-19 08:40 | 52.2 | F | 245 | F | zn
2015-02-20 14:45 | 46.5 | F | 290 | F | pf
2015-02-21 08:20 | 52 | F | 270 | F | zn
2015-02-22 10:00 | 53.4 | F | 280 | F | zn
2015-02-23 11:00 | 54.3 | F | 270 | F | zn
2015-02-24 10:15 | 50.4 | F | 345 | F | pf
2015-02-25 08:45 | 53.5 | F | 340 | F | zn
2015-02-26 11:30 | 54.6 | F | 260 | F | pf
2015-02-27 09:40 | 55.2 | F | 210 | F | zn
2015-02-28 08:20 | 54.7 | F | 185 | F | pf
2015-03-01 08:00 | 55.1 | F | 155 | F | zn
2015-03-02 08:55 | 55.6 | F | 180 | F | zn
2015-03-03 09:00 | 55.4 | F | 380 | F | pf
2015-03-04 09:20 | 53.7 | F | 265 | F | jp
2015-03-05 09:45 | 52.5 | F | 300 | F | zn
2015-03-06 08:10 | 51.7 | F | 65 | F | zn
2015-03-07 08:05 | 54.5 | F | 10 | F | zn
2015-03-08 10:24 | 54.8 | F | 25 | F | zn
2015-03-09 08:20 | 54.8 | F | 45 | F | zn
2015-03-10 08:25 | 54.7 | F | 290 | F | zn
2015-03-11 08:30 | 50.6 | F | 890 | F | zn
2015-03-12 08:00 | 53.7 | F | 415 | F | zn
2015-03-13 08:45 | 54 | F | 275 | F | zn
2015-03-14 11:00 | 52.8 | F | 265 | F | jp
2015-03-15 08:35 | 54.3 | F | 180 | F | jp
2015-03-16 08:50 | 54.6 | F | 515 | F | zn
2015-03-16 14:00 | 54.1 | F | 1050 | F | zn
2015-03-17 08:30 | 48.6 | F | 1555 | F | pf
2015-03-18 08:00 | 56.1 | F | 270 | F | zn
2015-03-19 08:00 | 57.8 | F | 180 | F | zn
2015-03-20 09:30 | 58 | F | 85 | F | jp
2015-03-21 09:00 | 58.4 | F | 205 | F | pf
2015-03-22 08:10 | 58 | F | 265 | F | pf
2015-03-23 08:15 | 57.5 | F | 260 | F | zn
2015-03-24 08:15 | 67.5 | w | 183 | w | zn
2015-03-24 08:15 | 57.4 | F | 275 | F | zn
2015-03-25 09:30 | 68.3 | w | 125 | w | jp
2015-03-25 09:30 | 56.9 | F | 130 | F | jp
2015-03-26 08:26 | 68.4 | w | 104 | w | zn
2015-03-26 08:26 | 58.7 | F | 83 | F | zn
2015-03-27 08:30 | 67.2 | w | 0 | w | zn
2015-03-27 08:30 | 57 | F | 385 | F | zn
2015-03-29 08:50 | 55.8 | F | 120 | F | jp
2015-03-30 09:30 | 69.5 | w | 0 | w | zn
2015-03-30 09:30 | 56.1 | F | 195 | F | zn
2015-03-31 08:20 | 65.3 | w | 0 | w | zn
2015-03-31 08:20 | 58.1 | F | 165 | F | zn
2015-04-01 08:35 | 65.8 | w |  |  | zn
2015-04-01 08:35 | 58.6 | F | 120 | F | zn
2015-04-02 08:40 | 64.9 | w |  |  | pf
2015-04-02 08:40 | 57 | F | 130 | F | pf
2015-04-04 07:50 | 64.9 | w |  |  | zn
2015-04-04 07:50 | 57.9 | F | 130 | F | zn
2015-04-06 08:57 | 64.8 | w |  |  | jp
2015-04-06 08:57 | 57.1 | F | 85 | F | jp
2015-04-07 08:10 | 57.1 | w |  |  | pf
2015-04-07 08:10 | 42.8 | F | 130 | F | pf
2015-04-08 09:50 | 64.1 | w |  |  | zn
2015-04-08 09:50 | 55.8 | F | 155 | F | zn
2015-04-09 08:15 | 63.9 | w |  |  | zn
2015-04-09 08:15 | 55.4 | F | 160 | F | zn
2015-04-10 09:47 | 63.3 | w |  |  | zn
2015-04-10 09:47 | 54.8 | F | 180 | F | zn
2015-04-11 09:00 | 63.2 | w |  |  | pf
2015-04-11 09:00 | 54.8 | F | 145 | F | pf
2015-04-12 11:00 | 63.3 | w |  |  | pf
2015-04-12 11:00 | 54.7 | F | 160 | F | pf
2015-04-13 08:00 | 63.2 | w |  |  | zn
2015-04-13 08:00 | 54.1 | F | 170 | F | zn
2015-04-14 09:00 | 63.1 | w |  |  | pf
2015-04-14 09:00 | 54.4 | F | 170 | F | pf
2015-04-15 09:40 | 63.4 | w | 172 | w | zn
2015-04-15 09:40 | 48.9 | F | 180 | F | zn
2015-04-16 08:30 | 62.5 | w | 1090 | w | zn
2015-04-16 08:30 | 48.3 | F | 185 | F | zn
2015-04-17 08:00 | 62.4 | w | 360 | w | pf
2015-04-17 08:00 | 54.7 | F | 170 | F | pf
2015-04-18 09:45 | 61.9 | w | 345 | w | zn
2015-04-18 09:45 | 61.6 | w | 288 | w | zn
2015-04-18 09:45 | 48.5 | F | 180 | F | zn
2015-04-18 09:45 | 48.4 | F | 155 | F | zn
2015-04-20 11:30 | 61.6 | w | 258 | w | zn
2015-04-21 08:20 | 60.4 | w | 283 | w | zn
2015-04-21 08:20 | 47.2 | F | 155 | F | zn
2015-04-22 08:50 | 46.5 | F | 95 | F | jp
2015-04-22 08:50 |  |  | 298 | w | jp
2015-04-23 08:10 | 60.7 | w | 323 | w | pf
2015-04-23 08:10 | 47.4 | F | 140 | F | pf
2015-04-24 08:20 | 61.1 | w | 265 | w | zn
2015-04-24 08:20 | 51.1 | F | 130 | F | zn
2015-04-25 09:40 | 46.9 | F | 75 | F | jp
2015-04-25 09:40 |  |  | 266 | w | jp
2015-04-26 08:40 | 49 | F | 50 | F | jp
2015-04-26 08:40 |  |  | 271 | w | jp
2015-04-27 09:45 | 60.8 | w | 203 | w | zn
2015-04-27 09:45 | 48.5 | F | 110 | F | zn
2015-04-28 08:10 | 60.5 | w | 268 | w | pf
2015-04-28 08:10 | 49 | F | 100 | F | pf
2015-04-29 08:40 | 60.7 | w | 328 | w | zn
2015-04-29 08:40 | 48.8 | F | 120 | F | zn
2015-04-30 08:10 | 60.8 | w | 292 | w | pf
2015-04-30 08:10 | 48.1 | F | 120 | F | pf
2015-05-01 14:00 | 60.3 | w | 222 | w | zn
2015-05-01 14:00 | 49.7 | F | 110 | F | zn
2015-05-02 10:30 | 50.1 | F | 50 | F | jp
2015-05-02 10:30 |  | w | 174 | w | jp
2015-05-03 09:10 | 49.9 | F | 40 | F | jp
2015-05-03 09:10 |  | w | 266 | w | jp
2015-05-06 08:45 | 62.3 | w | 194 | w | zn
2015-05-06 08:45 | 49.8 | F | 145 | F | zn
2015-05-07 09:50 | 61.2 | w | 364 | w | zn
2015-05-07 09:50 | 50.5 | F | 155 | F | zn
2015-05-08 10:00 | 61.4 | w | 289 | w | zn
2015-05-08 10:00 | 48 | F | 170 | F | zn
2015-05-10 09:15 | 60.7 | w | 369 | w | zn
2015-05-10 09:15 | 53.5 | F | 180 | F | zn
2015-05-11 08:55 | 60.5 | w | 350 | w | zn
2015-05-11 08:55 | 53.7 | F | 190 | F | zn
2015-05-12 08:35 | 60.3 | w | 275 | w | zn
2015-05-12 08:35 | 49.7 | F | 185 | F | zn
2015-05-13 08:45 | 60 | w | 262 | w | zn
2015-05-13 08:45 | 49.5 | F | 185 | F | zn
2015-05-14 09:15 | 60.5 | w | 342 | w | zn
2015-05-15 09:00 | 60.3 | w | 330 | w | zn
2015-05-16 11:00 | 60 | w | 323 | w | zn
2015-05-17 10:00 | 59.9 | w | 358 | w | dk
2015-05-18 08:03 | 59.6 | w | 432 | w | bb
2015-05-19 08:55 | 59.5 | w | 295 | w | zn
2015-05-21 08:40 | 60.2 | w | 320 | w | zn
2015-05-22 07:50 | 61.1 | w | 480 | w | zn
2015-05-23 07:58 | 62.3 | w | 329 | w | zn
2015-05-24 08:40 | 63.2 | w | 413 | w | zn
2015-05-25 09:00 | 63.2 | w | 333 | w | zn
2015-05-26 10:15 | 62 | w | 367 | w | zn
2015-05-27 08:20 | 61.8 | w | 400 | w | zn
2015-05-28 09:45 | 60.7 | w | 263 | w | zn
2015-05-29 08:15 | 61.9 | w | 196 | w | zn
2015-06-01 09:30 | 61.4 | w | 272 | w | zn
2015-06-02 08:15 | 61.1 | w | 300 | w | bb
2015-06-04 08:15 | 61.3 | w | 313 | w
2015-06-05 08:30 | 60.6 | w | 334 | w
2015-06-06 | 59.7 | w | 354 | w
2015-06-09 09:30 | 57.5 | w | 242 | w | zn
2015-06-10 08:22 | 60.3 | w | 521 | w | dr | calibrated analyzer
2015-06-11 15:30 | 60.8 | w | 435 | w | zn
2015-06-12 08:50 | 60.5 | w | 342 | w | bb
2015-06-13 07:20 | 59.8 | w | 487 | w | dr
2015-06-14 07:20 | 59.5 | w | 539 | w | dr
2015-06-15 15:00 | 58.9 | w | 275 | w | zn
2015-06-16 12:00 | 58.4 | w | 306 | w | zn
2015-06-17 07:30 | 58 | w | 399 | w | dr
2015-06-18 08:20 | 58.3 | w | 465 | w | zn
2015-06-19 08:45 | 57.7 | w | 368 | w | bb
2015-06-20 09:40 | 57.8 | w | 297 | w | zn
2015-06-21 08:00 | 57.2 | w | 378 | w | zn
2015-06-22 10:15 | 56.6 | w | 210 | w | zn
2015-06-23 08:00 | 56 | w | 298 | w | dr
2015-06-24 08:00 | 55.5 | w | 214 | w | dr
2015-06-25 07:40 | 55.9 | w | 130 | w | zn
2015-06-26 09:41 | 61.1 | w | 164 | w | zn | calibrated analyzer
2015-06-27 08:53 | 60.5 | w | 198 | w | dk
2015-06-28 08:39 | 60.2 | w | 272 | w | dk
2015-06-29 09:00 | 60.9 | w | 149 | w | bb
2015-06-30 09:00 | 59.5 | w | 265 | w | zn
2015-07-01 10:30 | 58.5 | w | 161 | w | zn
2015-07-02 09:10 | 58.3 | w | 146 | w | zn
2015-07-03 10:45 | 59.5 | w | 165 | w | zn
2015-07-04 07:30 | 60.5 | w | 243 | w | dk | calibrated analyzer
2015-07-05 07:15 | 60 | w | 248 | w | dr
2015-07-06 08:30 | 59.3 | w | 299 | w | dr
2015-07-07 08:30 | 57.6 | w | 347 | w | dr
2015-07-08 08:30 | 57.7 | w | 321 | w | dr
2015-07-09 09:00 | 56.2 | w | 265 | w | zn
2015-07-10 10:50 | 57.7 | w | 288 | w | zn | calibrated analyzer
2015-07-12 11:15 | 58.9 | w | 335 | w | bb
2015-07-13 07:35 | 59.1 | w | 338 | w | dr
2015-07-14 12:10 | 63.4 | w | 197 | w | zn
2015-07-15 09:15 | 63.7 | w | 154 | w | zn
2015-07-16 09:30 | 62.9 | w | 244 | w | zn
2015-07-17 08:45 | 62.4 | w | 169 | w | zn
2015-07-18 08:30 | 61.4 | w | 195 | w | bb
2015-07-19 08:20 | 60.2 | w | 187 | w | bb
2015-07-20 07:45 | 60.2 | w | 203 | w | dr
2015-07-20 10:00 | 62.1 | w | 181 | w | zn | calibrated analyzer
2015-07-21 08:10 | 61.5 | w | 91 | w | zn
2015-07-23 09:00 | 60.5 | w | 61 | w | bb
2015-07-24 07:40 | 60.3 | w | 105 | w | dr
2015-07-25 09:30 | 59.8 | w | 57 | w | zn
2015-07-26 08:30 | 60.4 | w | 20 | w | zn
2015-07-27 07:35 | 59.8 | w | 71 | w | dr
2015-07-28 08:21 | 58.8 | w | 46 | w | zn
2015-07-29 11:00 | 59.6 | w | 79 | w | zn
2015-07-30 08:00 | 58.9 | w | 98 | w | dr
2015-07-31 08:00 | 58.5 | w | 60 | w | dr
2015-08-01 07:45 | 58.4 | w | 54 | w | dr
2015-08-02 07:35 | 59.6 | w | 58 | w | dr
2015-08-03 08:20 | 59.8 | w | 49 | w | dk
2015-08-03 14:18 | 60.5 | w | 217 | w | zn | calibrated analyzer
2015-08-04 07:20 | 60.2 | w | 114 | w | dr
2015-08-05 09:00 | 60.6 | w | 129 | w | dr
2015-08-06 13:20 | 61.1 | w | 73 | w | zn
2015-08-07 09:15 | 59.9 | w | 82 | w | zn
2015-08-08 09:00 | 59.1 | w | 31 | w | dk
2015-08-09 08:45 | 59.4 | w | 59 | w | zn
2015-08-10 09:55 | 59 | w | 51 | w | zn
2015-08-11 10:00 | 58.8 | w | 122 | w | dk
2015-08-12 09:30 | 59.8 | w | 79 | w | zn
2015-08-14 11:59 | 60.4 | w | 221 | w | zn | calibrated analyzer
2015-08-15 08:10 | 60.4 | w | 106 | w | bb
2015-08-16 08:20 | 61 | w | 60 | w | bb
2015-08-17 09:25 | 61.9 | w | 47 | w | zn
2015-08-18 08:15 | 60.2 | w | 145 | w | zn
2015-08-19 08:15 | 60.4 | w | 165 | w | bb
2015-08-20 12:09 | 60.4 | w | 178 | w | zn
2015-08-21 09:08 | 60.2 | w | 132 | w | zn
2015-08-22 10:00 | 60.3 | w | 156 | w | zn
2015-08-23 08:30 | 60.9 | w | 207 | w | zn
2015-08-24 09:45 | 61.3 | w | 281 | w | zn | calibrated analyzer
2015-08-25 08:00 | 60.7 | w | 201 | w | zn
2015-08-26 07:45 | 60.5 | w | 175 | w | zn
2015-08-27 08:50 | 60 | w | 167 | w | zn
2015-08-29 11:30 | 60.9 | w | 164 | w | zn
2015-08-30 09:10 | 61.9 | w | 35 | w | zn
2015-08-31 09:08 | 62.6 | w | 1 | w | zn
2015-09-01 09:45 | 59.4 | w | 304 | w | zn | calibrated analyzer
2015-09-02 10:28 | 60.8 | w | 193 | w | bc
2015-09-03 09:00 | 62.2 | w | 119 | w | zn
2015-09-04 08:10 | 63.4 | w | 76 | w | zn
2015-09-04 09:10 | 63.1 | w | 167 | w | zn
2015-09-05 08:20 | 64.3 | w | 159 | w | zn
2015-09-06 08:41 | 65.5 | w | 51 | w | zn
2015-09-07 10:00 | 65.5 | w | 149 | w | zn
2015-09-08 08:00 | 65.7 | w | 133 | w | zn
2015-09-09 08:00 | 65.6 | w | 159 | w | zn
2015-09-11 08:59 | 65.6 | w | 46 | w | bc
2015-09-12 10:30 | 64.4 | w | 132 | w | jrh
2015-09-12 10:30 |  |  | 214 | w | jrh
2015-09-13 08:00 | 63.9 | w | 168 | w | dk | genset offline
2015-09-19 09:00 | 62.2 | w | 0 | w | zn
2015-09-19 09:57 | 60.4 | w | 72 | w | zn
2015-09-20 09:10 | 63 | w | 208 | w | zn
2015-09-21 11:00 | 64.5 | w | 18 | w | zn | calibrated analyzer
2015-09-22 08:00 | 64.9 | w | 3 | w | zn
2015-09-22 10:10 |  |  | 118 | w | zn
2015-09-23 08:20 | 64.6 | w | 73 | w | bc
2015-09-24 08:00 | 65.1 | w | 7 | w | zn
2015-09-25 11:12 | 64.2 | w | 15 | w | zn
2015-09-26 08:35 | 64.8 | w | 7 | w | dk
2015-09-27 10:36 | 63.5 | w | 13 | w | dk
2015-09-28 09:40 | 65.2 | w | 0 | w | bc
2015-09-28 12:48 | 62.8 | w | 60 | w | zn
2015-09-29 08:53 | 63.4 | w | 43 | w | zn
2015-09-30 09:15 | 64.4 | w | 76 | w | bc
2015-10-01 08:00 | 65.8 | w | 84 | w | zn
2015-10-02 07:54 | 64.6 | w | 103 | w | zn
2015-10-03 08:00 | 64.5 | w | 65 | w | zn
2015-10-04 08:00 | 63.3 | w | 63 | w | zn
2015-10-05 08:20 | 63.5 | w | 182 | w | zn
2015-10-06 08:20 | 64 | w | 174 | w | bc
2015-10-07 10:21 | 63.2 | w | 200 | w | bc
2015-10-08 07:49 | 63.6 | w | 188 | w | zn
2015-10-09 08:45 | 63.3 | w | 190 | w | bc
2015-10-10 09:40 | 62.6 | w | 252 | w | dk
2015-10-12 08:20 | 62.9 | w | 230 | w | zn
2015-10-13 09:30 | 60.9 | w | 242 | w | zn
2015-10-13 11:15 | 58.4 | w | 315 | w | zn | calibrated analyzer
2015-10-14 08:00 | 61.6 | w | 265 | w | zn
2015-10-15 08:20 | 61.1 | w | 261 | w | zn
2015-10-16 09:15 | 60.4 | w | 270 | w | zn
2015-10-17 08:00 | 61 | w | 277 | w | zn
2015-10-18 09:57 | 62.5 | w | 240 | w | zn
2015-10-19 09:11 | 63 | w | 259 | w | bc
2015-10-20 08:59 | 61.2 | w | 233 | w | zn
2015-10-21 09:05 | 61.7 | w | 216 | w | zn | beginning of automatically logged biogas quality info, look on vtc's database server. Vtcsqlv 12, BC30_Data, SQL-Server Auth., BC30user, BC30user
2015-10-22 07:30 | 61.5 | w | 198 | w | dk
2015-10-23 10:18 | 60.4 | w | 197 | w | bc
2015-10-24 09:18 | 60.1 | w | 175 | w | dk
2015-10-25 08:00 | 61.3 | w | 148 | w | dk
2015-10-26 08:05 | 61.3 | w | 170 | w | zn
2015-10-27 08:53 | 60 | w | 250 | w | zn
2015-10-28 10:03 | 60.1 | w | 224 | w | dk
2015-10-29 08:00 | 61 | w | 147 | w | zn
2015-10-30 09:11 | 62.5 | w | 137 | w | bc
2015-10-31 09:12 | 60.9 | w | 140 | w | bc
2015-11-01 07:10 | 64 | w | 52 | w | bc
2015-11-02 07:00 | 64.7 | w | 174 | w | bc
2015-11-03 08:05 | 64.9 | w | 163 | w | zn
2015-11-04 06:30 | 64.1 | w | 174 | w | bc
2015-11-05 08:15 | 64.2 | w | 248 | w | zn
2015-11-06 08:19 | 62.7 | w | 234 | w | zn
2015-11-07 08:03 | 61.8 | w | 584 | w | zn
2015-11-08 08:00 | 62.5 | w | 430 | w | zn
2015-11-10 07:54 | 61.7 | w | 244 | w | zn
2015-11-11 08:38 | 63 | w | 179 | w | bc
2015-11-12 09:00 | 64.3 | w | 206 | w | zn
2015-11-13 08:23 | 63 | w | 201 | w | bc
2015-11-14 10:10 | 62.7 | w | 170 | w | bc
2015-11-15 07:45 | 62.7 | w | 125 | w | bc
2015-11-16 09:58 | 63.4 | w | 270 | w | zn
2015-11-17 07:25 | 63.4 | w | 112 | w | dk
2015-11-18 08:15 | 64.3 | w | 167 | w | bc
2015-11-19 08:00 | 63.8 | w | 263 | w | zn
2015-11-20 09:55 | 64.7 | w | 192 | w | bc
2015-11-21 10:00 | 63.6 | w | 266 | w | zn
2015-11-22 10:00 | 63.7 | w | 267 | w | zn
2015-11-23 09:40 | 62.6 | w | 283 | w | zn
2015-11-24 08:40 | 62.8 | w | 184 | w | zn
2015-11-25 09:00 | 62.9 | w | 222 | w | dk
2015-11-26 07:50 | 63.7 | w | 278 | w | dk
2015-11-27 09:35 | 62.8 | w | 289 | w | bc
2015-11-28 08:15 | 61.1 | w | 353 | w | dk
2015-11-29 07:50 | 64.4 | w | 292 | w | dk
2015-11-30 08:25 | 66 | w | 229 | w | bc
2015-12-01 08:55 | 65.2 | w | 382 | w | zn
2015-12-02 07:40 | 64.5 | w | 467 | w | bc
2015-12-03 08:30 | 63.4 | w | 650 | w | zn | h2s 752 at 10:30
2015-12-04 07:35 | 64.2 | w | 394 | w | bc
2015-12-05 09:00 | 62 | w | 659 | w | zn
2015-12-06 08:00 | 62.1 | w | 772 | w | zn
2015-12-07 07:40 | 64.4 | w | 339 | w | bc
2015-12-08 09:30 | 62.6 | w | 443 | w | zn
2015-12-09 09:36 | 61.9 | w | 436 | w | bc
2015-12-10 11:11 | 58.2 | w | 669 | w | zn
2015-12-11 08:56 | 60.5 | w | 489 | w | bc
2015-12-12 07:45 | 60.8 | w | 581 | w | bc
2015-12-13 07:45 | 64 | w | 312 | w | bc
2015-12-14 07:35 | 63.6 | w | 310 | w | bc
2015-12-15 08:00 | 63.4 | w | 242 | w | zn

## pH
datetime | Hydrolyzer pH | Digester pH | ref. 7.01 | ref. 4.01 |  | e1 pH | tap | Digester BOT | notes
2014-06-13 10:00 |  | 6.6
2014-06-16 10:00 |  | 6.6
2014-06-17 09:30 |  | 6.7
2014-06-18 09:00 |  | 7.1
2014-06-19 09:30 |  | 7.4 |  |  |  |  | 8.4
2014-06-20 08:40 | 6 | 7.5 |  |  |  |  | 8.3
2014-06-23 10:30 | 6.2 | 7.45 |  |  |  |  | 8.2
2014-06-24 08:30 | 6.67 | 7.54 |  |  |  |  | 8.3
2014-06-25 07:30 | 6.51 | 7.34 |  |  |  |  | 8.1
2014-06-30 10:30 | 6.64 | 7.35 |  |  |  |  | 8.1
2014-07-01 07:30 | 6.67 | 7.34 |  |  |  |  | 8.1
2014-07-02 14:30 |  | 7.4 |  |  |  |  | 7.8
2014-07-03 07:30 |  | 7.4
2014-07-07 08:30 | 6.8 | 7.6 |  |  |  |  | 8.2
2014-07-08 07:30 | 7 | 7.6
2014-07-09 10:00 | 6.8 | 7.6
2014-07-10 07:30 |  | 7.6
2014-07-14 09:00 | 6.6 | 7.6 |  |  |  |  | 8.1
2014-07-15 07:30 | 6.9 | [5 empty] | 8.1
2014-07-21 09:30 | 6.96 | 7.61 |  |  |  |  | 8.1
2014-07-23 08:00 | 7.03 | 7.65 |  |  |  |  | 8.2
2014-07-24 07:30 | 7.11 | 7.62 |  |  |  |  | 8.1
2014-07-28 08:00
2014-07-29 07:30 | 7.15 | 7.51 |  |  |  |  | 8.06
2014-07-30
2014-08-01 14:00 | 7.11 | 7.56
2014-08-04
2014-08-05 10:00 | 7.1 | 7.5 |  |  |  |  | 8.04
2014-08-06 09:30 | 7.11 | 7.64 |  |  |  |  | 8.05
2014-08-07 15:00 | 6.92 | 7.54 |  |  |  |  | 8.1
2014-08-08 09:00
2014-08-12 10:00 | 6.93 | 7.59 |  |  |  |  | 8.1
2014-08-13 07:30
2014-08-14 13:30 | 6.89 | 7.61
2014-08-15 15:45 | 7.15 | 7.62 |  |  |  |  | 8.1
2014-08-19 14:45 | 7.4 | 7.5
2014-08-20 15:45 | 7.26 | 7.41 |  |  |  |  | 8.04
2014-08-21
2014-08-22 10:37 | 6.98 | 7.65
2014-08-25 07:00 | 6.57 | 7.6 |  |  |  |  | 8.1
2014-08-26 08:00 | 6.48 | 7.6
2014-08-27 08:30 | 6.32 | 7.68 |  |  |  |  | 7.98
2014-08-28 07:30 | 5.98 | 7.6
2014-08-29 07:30 | 5.84 | 7.61 |  |  |  |  | 7.92
2014-09-02
2014-09-03
2014-09-04 10:30 | 6.48 | 7.64
2014-09-05 08:30 | 6.67 | 7.58
2014-09-08 07:30 | 6.92 | 7.67
2014-09-09 10:30 | 6.8 | 7.5
2014-09-10 07:00 | 7 | 7.64
2014-09-11 07:00 | 7.08 | 7.69
2014-09-12 07:00 | 7.1 | 7.6
2014-09-15 09:00 | 7.45 | 7.71
2014-09-16 09:00 | 7.47 | 7.77
2014-09-17 09:00
2014-09-18 09:00 | 7.45 | 7.68
2014-09-19 13:00 | 7.43 | 7.68
2014-09-22 07:30 | 7.46 | 7.81
2014-09-23 10:00 | 7.23 | 7.49
2014-09-24 09:00 | 7.21 | 7.55
2014-09-25 15:00 | 7.23 | 7.6
2014-09-26 11:30 | 7.47 | 7.6
2014-09-27 17:00 | 5.97 | 7.33
2014-09-28 10:30 | 6.35 | 7.51
2014-09-29 08:30 | 6.29 | 7.43
2014-09-30 07:30 | 5.93 | 7.73
2014-10-01 08:00 | 5.76 | 7.48
2014-10-02 09:00 | 6.01 | 7.52
2014-10-03 09:00 | 5.95 | 7.5
2014-10-05 18:37 | 5.94 | 7.28
2014-10-06 | 6.3 | 7.4
2014-10-07 10:00 | 6.8 | 7.4
2014-10-08 08:00 | 6.5 | 7.4
2014-10-09 09:30 | 6.72 | 7.42 |  |  |  | 7.43
2014-10-10 10:00
2014-10-11 16:00 | 6.68 | 7.54 |  |  |  | 7.77
2014-10-12 17:45
2014-10-13 09:30 | 5.71 | 7.43 |  |  |  | 7.64
2014-10-14 09:00 | 6.02 | 7.44 |  |  |  | 7.59
2014-10-15 08:24 | 5.95 | 7.5 |  |  |  | 7.48 | 8.01
2014-10-16 08:30 | 6.2 | 7.5 |  |  |  | 7.62 | 7.98
2014-10-17 08:10 | 5.91 | 7.57 |  |  |  | 7.68 | 8.01
2014-10-18 13:15
2014-10-19 18:42
2014-10-20 08:30 | 6.1 | 7.71 |  |  |  | 7.8
2014-10-21 08:30 | 5.87 | 7.52 |  |  |  | 7.85 | 8.09
2014-10-22 08:00 | 5.86 | 7.61
2014-10-23 08:00 | 5.97 | 7.62 |  |  |  | 7.62
2014-10-23 16:50
2014-10-24 08:30 | 6.7 | 7.54 |  |  |  | 7.75 | 8.07
2014-10-25 16:30
2014-10-26 17:30
2014-10-27 07:00 | 6.36 | 7.5 |  |  |  |  | 7.3
2014-10-28 08:00 | 6.54 | 7.57 |  |  |  | 7.68 | 8.01
2014-10-29 11:30 | 7.37 | 7.56 |  |  |  | 7.67
2014-10-30 08:30 | 6.39 | 7.46 |  |  |  | 7.58
2014-10-31 08:00 | 6.67 | 7.58
2014-11-03 07:30 | 6.68 | 7.59 |  |  |  | 7.64 | 8.1
2014-11-04 08:00 | 6.39 | 7.5 |  |  |  | 7.6
2014-11-05 08:30 | 6.16 | 7.5 |  |  |  | 7.6 | 7.98
2014-11-06 07:30 | 6 | 7.53 |  |  |  |  | 7.95
2014-11-07 07:30 | 6.16 | 7.58
2014-11-10 07:55 | 6.33 | 7.65 |  |  |  |  | 7.93
2014-11-11 08:30 | 6.43 | 7.6
2014-11-12 08:15 | 6.34 | 7.69 |  |  |  | 7.7 | 8.05
2014-11-13 07:15 | 6.59 | 7.69
2014-11-14 08:15 | 6.31 | 8.32 |  |  |  | 8.11 | 8.3
2014-11-17 08:30 | 6.68 | 7.71
2014-11-18 08:20 | 6.42 | 7.79 |  |  |  |  | 8.23
2014-11-19 08:20 | 6.39 | 7.75
2014-11-20 07:30 | 6.26 | 7.77 |  |  |  |  | 8.08
2014-11-21 09:20
2014-11-24 08:40 | 6.5 | 8.01
2014-11-25 08:30 | 6.82 | 7.71
2014-11-26 09:45 | 7.05 | 7.67
2014-11-28 08:30 | 6.93 | 7.78
2014-12-01 08:00 | 7.09 | 7.68
2014-12-02 08:00 | 7.14 | 7.8
2014-12-03 09:50 | 7.08 | 7.84
2014-12-04 08:00 | 6.79 | 7.86
2014-12-05 09:15 | 6.58 | 7.71
2014-12-08 11:30
2014-12-09 09:30 | 6.64 | 7.79 |  |  |  | 7.69
2014-12-10 09:30 | 6.12 | 7.74
2014-12-11 08:45 | 5.7 | 7.79
2014-12-12 08:15 | 5.77 | 7.74
2014-12-14 09:00 | 6 | 7.1
2014-12-17 08:30 | 6.16 | 7.75 |  |  |  | 7.88
2014-12-18 08:00 | 6.1 | 7.66
2014-12-19 10:00 | 5.92 | 7.6
2014-12-22 08:45 | 5.47 | 7.65
2014-12-23 08:00 | 5.65 | 7.66
2014-12-24 09:50 | 5.97 | 7.65
2014-12-25 07:50 | 5.75 | 7.57
2014-12-26 08:00 | 5.85 | 7.67
2014-12-29 08:30 | 5.54 | 7.54
2014-12-30 07:30 | 5.49 | 7.78
2014-12-31 08:00 | 5.35 | 7.71
2015-01-02 07:45 | 5.46 | 7.72
2015-01-05 08:00 | 5.57 | 7.64
2015-01-06 08:15 | 5.56 | 7.68
2015-01-07 09:00 | 5.9 | 7.74
2015-01-08 07:50 | 5.76 | 7.75
2015-01-09 08:40 | 5.75 | 7.71
2015-01-10 09:00 | 5.76 | 7.68
2015-01-11 11:20 | 5.72 | 7.67
2015-01-12 07:39 | 6.1 | 7.76
2015-01-13 08:00 | 5.79 | 7.8
2015-01-14 08:50 | 5.84 | 7.62 | 7.22 | 4.37
2015-01-15 07:30 | 5.76 | 7.51 | 7.16 | 4.27
2015-01-16 09:00 | 5.62 | 7.66 | 7.21 | 4.39
2015-01-17 08:20 | 5.58 | 7.65 | 7.17 | 4.34
2015-01-18 14:00 | 5.41 | 7.59
2015-01-19 08:45 | 5.87 | 7.47 | 7.23 | 4.38
2015-01-20 09:13 | 5.74 | 7.77 | 7.12 | 4.35
2015-01-22 07:45
2015-01-23 08:15 | 5.69 | 7.59 | 7.1 | 4.27
2015-01-24 08:50 | 5.6 | 7.57 | 7.11 | 4.26 |  |  |  | 7.45
2015-01-25 08:25 | 5.69 | 7.47 | 7.09 | 4.27
2015-01-26 07:50 | 5.73 | 7.43
2015-01-27 09:30
2015-01-28 09:30
2015-01-29 08:00 | 6.17 | 7.67 | 7.25 | 4.29
2015-01-30 08:45 |  | 7.63 | 7.15 | 4.27
2015-02-02 08:30 | 6.1 | 7.56 | 7.12 | 4.24 | zn
2015-02-03 08:45 | 6.19 | 7.64 | 7.19 | 4.28 | zn
2015-02-04 14:50 | 6.28 | 7.73 | 7.27 | 4.33 | zn
2015-02-05 08:30 | 6.16 | 7.71 | 7.16 | 4.27 | zn
2015-02-06 08:45 | 6.08 | 7.58 | 7.16 | 4.29 | zn
2015-02-07 08:00 | 6.11 | 7.66 | 7.16 | 4.34 | zn
2015-02-08 09:15 | 6.11 | 7.63 | 7.17 | 4.27 | zn
2015-02-09 12:15 | 6.23 | 7.69 | 7.15 | 4.34 | jp
2015-02-10 10:00 | 6.27 | 7.73 | 7.2 | 4.32 | zn
2015-02-11 09:00 | 6.14 | 7.66 | 7.11 | 4.34 | zn
2015-02-12 09:45 | 6.24 | 7.57 | 7.08 | 4.31 | zn
2015-02-13 10:50 | 6.13 | 7.55 |  |  | zn
2015-02-14 08:30 | 6.1 | 7.56 | 7.06 | 4.22 | jp
2015-02-15 09:30 | 6.2 | 7.71 | 7.23 | 4.24 | jp
2015-02-17 09:50 | 5.81 | 7.78 | 7.3 | 4.42 | zn
2015-02-18 13:30 | 6.05 | 7.54 | 7.05 |  | zn
2015-02-19 10:30 | 5.92 | 7.58 | 7.03 | 4.27 | zn
2015-02-21 07:50 | 5.73 | 7.54 | 7.06 | 4.24 | zn
2015-02-22 08:30 | 5.6 | 7.53 | 7.03 | 4.19 | zn
2015-02-23 09:15 | 5.59 | 7.54
2015-02-25 09:30 | 5.2 | 7.57 | 7.07 | 4.27 | zn
2015-02-27 09:55 | 5.26 | 7.59 | 7.08 | 4.3 | zn
2015-03-01 11:00 | 5.19 | 7.58 | 7.09 | 4.28 | zn
2015-03-02 09:30 | 5.16 | 7.61 | 7.15 | 4.3 | zn
2015-03-04 15:30 | 5.3 | 7.54 | 7.04 | 4.26 | jp
2015-03-05 02:20 | 5.41 | 7.64 | 7.1 | 4.37 | zn
2015-03-06 15:00 | 5.61 | 7.62 | 7.14 | 4.45 | zn
3/7/2015 1500 | 5.59 | 7.57 |  |  | zn
2015-03-08 12:35 | 5.61 | 7.56 | 7.12 | 4.36 | zn
2015-03-10 12:15 | 5.57 | 7.68 | 7.16 | 4.25 | zn |  |  |  | fresh ref. solution
2015-03-11 10:15 | 5.42 | 7.67 | 7.17 | 4.45 | jp
2015-03-12 09:30 | 5.56 | 7.68 | 7.17 | 4.61 | zn |  |  |  | suspect contaminated solution
2015-03-13 11:45 | 5.57 | 7.6 | 7.18 | 4.48 | jp
2015-03-14 11:30 | 5.69 | 7.58 | 7.2 | 4.46 | jp
2015-03-15 11:00 | 5.57 | 7.46 | 7.14 | 4.37 | jp
2015-03-18 10:30 | 5.47 | 7.37 | 7.14 | 4.54 | zn |  |  |  | cold in middle bay
2015-03-19 09:30 | 5.48 | 7.54 | 7.11 | 4.33 | zn
2015-03-20 11:00 | 5.51 | 7.52 |  |  | jp
2015-03-22 08:40 | 5.15 | 7.27 | 7.12 | 4.47 | pf
2015-03-23 15:40 | 5.17 | 7.47 | 7.11 | 4.27 | zn |  |  |  | fresh ref. solution. Oily hydrolyzer juice hard to remove from probe
2015-03-24 08:50 | 5.08 | 7.45 | 7.11 | 4.26 | zn |  |  |  | cleaned probe with toothbrush and dishsoap after oily hydrolyzer sample
2015-03-25 15:00 | 5.03 | 7.5 | 7.12 | 4.25 | zn
2015-03-26 14:00 | 5.05 | 7.52 | 7.14 | 4.32 | zn
2015-03-27 09:30 | 5.06 | 7.43 | 7.12 |  | zn
2015-03-28 11:15 | 4.89 | 7.51 | 7.13 | 4.35 | jp
2015-03-29 10:55 | 4.91 | 7.74 | 7.1 | 4.3 | jp
2015-03-30 15:20 | 4.92 | 7.58 | 7.14 |  | zn |  |  |  | fresh 7 buffer. Need distilled water to mix up more 4
2015-03-31 10:25 | 4.92 | 7.74 |  |  | zn
2015-04-01 14:40 | 4.96 | 7.5 |  |  | zn
2015-04-04 12:30 | 4.82 | 7.91 | 7.05 |  | zn
2015-04-06 13:30 | 4.84 | 7.4 | 7.09 |  | jp
2015-04-07 10:00 | 4.85 | 7.69 | 7.14 |  | zn |  |  |  | shallow depth of 7.01
2015-04-08 13:20 | 4.8 | 7.35 | 7.08 | 4.21 | zn
2015-04-09 10:00 | 4.82 | 7.51 | 7.08 | 4.2 | zn
2015-04-10 10:30 | 4.89 | 7.46 | 7.09 | 4.21 | zn
2015-04-13 09:22 | 4.88 | 7.33 | 7.05 | 4.22 | zn
2015-04-14 10:30 | 4.96 | 7.39 | 7.11 | 4.22 | zn
2015-04-15 09:30 | 5 | 7.45 | 7.11 | 4.29 | zn |  |  |  | need fresh 4.0
2015-04-16 10:20 | 5.02 | 7.35 |  |  | zn
2015-04-17 10:30 | 5.04 | 7.34 | 7.09 | 4.18 | zn |  |  |  | fresh pH solutions
2015-04-18 10:30 | 5.11 | 7.36 | 7.09 | 4.21 | zn
2015-04-19 10:50 | 5.14 | 7.36 | 7.07 | 4.22 | zn
2015-04-20 02:50 | 5.18 | 7.39 | 7.06 | 4.2 | jp
2015-04-21 09:55 | 5.08 | 7.54 | 7.07 | 4.21 | zn
2015-04-22 11:00 | 5.15 | 7.5 | 7 | 4.21 | jp
2015-04-23 08:30 | 5.08 | 7.43 | 7.1 | 4.18 | pf
2015-04-24 10:45 | 5.03 | 7.35 | 7.07 | 4.28 | zn
2015-04-25 09:00 | 5.02 | 7.37 | 7.06 | 4.24 | jp
2015-04-26 08:50 | 5.04 | 7.3 | 7.04 | 4.26 | jp
2015-04-27 13:00 | 5.18 | 7.32 | 7.1 | 4.29 | zn
2015-04-28 14:15 | 5.22 | 7.23
2015-04-29 13:45 | 5.18 | 7.19 | 7.08 | 4.26 | zn
2015-04-30 13:00 | 5.08 | 7.22 | 7.08 |  | zn
2015-05-01 14:00 | 5.02 | 7.22
2015-05-02 10:30 | 5.06 | 7.22 | 7.03 |  | jp
2015-05-03 09:30 | 5.04 | 7.22 | 7.04 |  | jp
2015-05-06 09:50 | 5.1 | 7.23 | 7.11 |  | zn
2015-05-07 13:18 | 5.03 | 7.18 | 7.01 |  | zn
2015-05-08 13:15 | 5.02 | 7.24 | 7.05 |  | zn
2015-05-12 09:00 | 5.25 | 7.17 | 7.04 |  | zn
2015-05-13 10:30 | 5.25 | 7.23 | 7.07 |  | zn
2015-05-15 09:00 | 5.14 | 7.32 |  |  | zn |  |  |  | pasco meter
2015-05-16 11:00 | 5.19 | 7.15
2015-05-18 11:10 | 5.35 | 7.13 | 7.07 |  | zn | 7.34
2015-05-19 09:30 | 5.13 | 7.13 | 7.09 |  | zn
2015-05-21 11:00 | 5.04 | 7.21 |  |  | zn |  |  |  | pasco
2015-05-23 10:15 | 5.19 | 7.13 | 7.14 |  | zn
2015-05-25 09:00 | 5.11 | 7.13 | 7.01 |  | zn |  |  |  | fresh 7.01 solution
2015-05-26 10:10 | 5.43 | 7.05 | 7.02 |  | zn
2015-05-27 08:30 | 5.19 | 7.03 | 7.02 |  | zn
2015-05-28 09:30 | 5.13 | 6.99 | 7 |  | zn
2015-05-29 09:15 | 5.35 | 7.12 | 7.02
2015-06-01 08:40 | 5.35 | 7.02 | 7.05 |  | zn |  |  |  | does the pH meter read higher when air temperature is colder?
2015-06-04 10:30 | 5.15 | 7.02 | 6.94 | 4.07 | zn
2015-06-08 | 5.34 | 7.09 | 7.02 | 4.12 | zn
2015-06-09 | 5.08 | 7.06 | 7.03 | 4.12 | zn
2015-06-11 08:30 | 4.97 | 7.04 | 6.99 | 4.19 | zn
2015-06-12 09:00 | 4.88 | 7.11
2015-06-16 14:00 | 5.16 | 7.09 | 7 | 4.09 | zn
2015-06-17 12:00 | 5.1 | 7.1 |  |  | dr
2015-06-18 13:45 | 5.2 | 7.16 |  |  | bb
2015-06-19 11:20 | 5.2 | 7.14 |  |  | bb
2015-06-20 11:15 | 5.16 | 7.13 |  |  | zn
2015-06-21 12:00 | 5.15 | 7.11 |  |  | zn
2015-06-22 09:40 | 5.25 | 7.16 |  |  | zn
2015-06-23 08:20 | 5.42 | 7.12 |  |  | dr
2015-06-24 08:10 | 5.29 | 7.12 |  |  | dr
2015-06-25 10:30 | 5.27 | 7.18 | 6.98 | 4.13 | zn
2015-06-26 10:00 | 5.12 | 7.21 |  |  | zn
2015-06-27 09:00 | 5.15 | 7.2 |  |  | dk
2015-06-28 08:20 | 5.23 | 7.15 |  |  | dk
2015-06-29 09:00 | 5.41 | 7.19 |  |  | bb
2015-06-30 09:35 | 5.53 | 7.18 |  |  | zn
2015-07-01 09:00 | 5.45 | 7.23 |  |  | zn
2015-07-02 09:30 | 5.21 | 7.19 |  |  | zn
2015-07-03 10:45 | 5.48 | 7.2 |  |  | zn
2015-07-04 07:33 | 5.45 | 7.18 |  |  | dk
2015-07-05 07:15 | 5.47 | 7.13 |  |  | dr |  |  |  | pH tester left out to dry yesterday
2015-07-06 08:00 | 5.53 | 7.16 |  |  | dr
2015-07-07 08:30 | 5.58 | 7.14 |  |  | dr
2015-07-08 08:50 | 5.58 | 7.13 |  |  | dr
2015-07-09 11:10 | 5.57 | 7.13 | 7.04 | 4.21 | zn
2015-07-10 10:30 | 5.55 | 7.13 |  |  | zn
2015-07-13 08:20 | 5.63 | 7.08 |  |  | dr
2015-07-14 08:30 | 5.58 | 7.22 |  |  | dr
2015-07-15 08:20 | 5.45 | 7.26 |  |  | zn
2015-07-16 09:00 | 5.52 | 7.29 |  |  | zn
2015-07-17 09:20 | 5.31 | 7.29 | 6.97 | 4.25 | zn
2015-07-20 07:50 | 5.09 | 7.3 |  |  | dr
2015-07-21 13:45 | 5.1 | 7.39 |  |  | zn |  |  |  | pasco
2015-07-23 09:00 | 5.19 | 7.38 |  |  | dr
2015-07-24 07:55 | 5.1 | 7.26 |  |  | dr
2015-07-25 11:50 | 5.22 | 7.28 |  |  | zn
2015-07-26 11:00 | 5.31 | 7.3 |  |  | zn
2015-07-27 07:52 | 5.3 | 7.33 |  |  | dr
2015-07-28 02:20 | 5.16 | 7.34 | 6.97 | 4.24 | zn
2015-07-29 14:00 | 5.14 | 7.24 |  |  | zn
2015-07-30 08:00 | 5.11 | 7.29 |  |  | dr
2015-07-31 07:44 | 5.24 | 7.23 |  |  | dr
2015-08-01 07:50 | 4.99 | 7.35 |  |  | dr
2015-08-02 07:40 | 5.01 | 7.32 |  |  | dr
2015-08-03 08:30 | 5.13 | 7.32 |  |  | dk
2015-08-05 09:30 | 4.97 | 7.33
2015-08-06 13:30 | 4.96 | 7.44 |  |  | zn
2015-08-07 09:00 | 5.03 | 7.31 |  |  | zn
2015-08-08 10:00 | 5.05 | 7.31 |  |  | dk
2015-08-09 09:25 | 5.03 | 7.28 |  |  | zn
2015-08-10 11:20 | 5.18 | 7.32 |  |  | zn
2015-08-11 09:15 | 5.04 | 7.43 |  |  | zn
2015-08-12 10:50 | 4.9 | 7.32 |  |  | zn
2015-08-14 11:44 | 4.98 | 7.31 |  |  | zn
2015-08-16 08:00 | 4.99 | 7.32 |  |  | bb
2015-08-17 11:12 | 5.07 | 7.33 | 6.93 | 3.96 | zn |  |  |  | fresh ref. solution.
2015-08-18 09:10 | 4.96 | 7.36 |  |  | zn
2015-08-19 09:00 | 4.9 | 7.3 |  |  | bb
2015-08-21 11:20 | 5.04 | 7.32 |  |  | zn
2015-08-22 10:50 | 5 | 7.31 |  |  | zn
2015-08-23 09:35 | 5.305 | 7.35 |  |  | dk
2015-08-24 13:00 |  | 7.52 |  |  | zn |  |  |  | pasco
2015-08-25 10:15 | 4.92 | 7.31 |  |  | zn
2015-08-26 09:15 | 4.87 | 7.35 |  |  | zn
2015-08-27 09:00 | 4.9 | 7.34 |  |  | zn
2015-08-29 12:00 | 4.93 | 7.28 |  |  | dk
2015-08-30 09:27 | 5.07 | 7.26 |  |  | zn
2015-08-31 14:00 | 5.07 | 7.43 |  |  | zn |  |  |  | pasco
2015-09-01 10:25 | 4.9 | 7.27 |  |  | zn
2015-09-02 11:34 | 4.83 | 7.28 |  |  | bc
2015-09-03 10:30 | 4.88 | 7.25 |  |  | zn
2015-09-04 11:23 | 4.77 | 7.28 |  |  | bc
2015-09-05 09:30 | 4.77 | 7.23 |  |  | zn
2015-09-06 12:25 | 4.8 | 7.22 |  |  | zn
2015-09-07 09:50 | 5.04 | 7.15 |  |  | zn
2015-09-08 08:30 | 4.93 | 7.18 |  |  | zn
2015-09-11 09:19 | 4.73 | 7.12 |  |  | bc
2015-09-12 10:30 | 4.88 | 7.4 |  |  | jrh
2015-09-13 08:00 | 4.92 | 7.08 |  |  | dk
2015-09-14 08:30 | 4.88 | 7.12 |  |  | zn
2015-09-15 09:00 | 4.92 | 7.13 |  |  | zn
2015-09-16 09:50 | 4.87 |  |  |  | bc | 7.24
2015-09-17 10:45 | 4.92 | 7.11 |  |  | zn
2015-09-18 09:30 | 5.06 | 7.12 |  |  | bc
2015-09-19 09:50 | 5.02 | 7.09 |  |  | zn
2015-09-20 11:30 | 5.15 | 7.01 |  |  | zn
2015-09-21 11:07 | 5.08 |  |  |  | bc | 7.18
2015-09-22 10:00 | 5.16 | 6.98 |  |  | zn
2015-09-23 09:12 | 5.13 | 7.06 |  |  | bc
2015-09-25 09:37 | 5.14 | 6.92 |  |  | bc
2015-09-26 08:35 | 4.98 | 7.04 |  |  | dk
2015-09-27 10:40 | 4.98 | 7 |  |  | dk
2015-09-28 10:51 | 4.97 |  |  |  | bc |  |  |  | feeding to digester off during pmp5 seal replacement. no flow out from digester
2015-09-29 10:19 | 4.99 | 6.98 |  |  | zn
2015-09-30 09:25 | 5.02 | 7.21 |  |  | zn
2015-10-01 09:10 | 5.04 | 7.21 |  |  | zn
2015-10-02 11:34 | 4.98 | 7.05 |  |  | bc
2015-10-04 10:30 | 4.87 | 7.14 |  |  | zn
2015-10-05 09:14 | 4.87 | 7.22 |  |  | zn
2015-10-06 10:14 | 4.89 | 7.05 |  |  | bc
2015-10-07 10:30 | 4.85 | 7.03 |  |  | bc
2015-10-08 08:55 | 5.04 | 7.12 |  |  | zn
2015-10-09 09:16 | 5.09 | 7.32 |  |  | bc
2015-10-10 09:38 | 5.37 | 7.15 |  |  | dk
2015-10-11 09:48 | 5.48 | 7.06 |  |  | dk
2015-10-12 09:00 | 5.6 | 7.08 |  |  | zn
2015-10-13 09:00 | 5.58 | 7.13 |  |  | zn
2015-10-14 09:44 | 5.58 | 7.2 | 6.63 | 3.8 | zn
2015-10-15 10:00 | 5.57 | 7.07 |  |  | zn
2015-10-16 13:41 | 5.59 | 7.21 |  |  | zn
2015-10-17 12:00 | 5.6 | 7.18 |  |  | zn
2015-10-18 11:20 | 5.55 | 7.4 |  |  | zn
2015-10-19 11:30 | 5.93 | 7.23 |  |  | bc
2015-10-20 08:50 | 5.42 | 7.14 |  |  | zn
2015-10-21 09:51 | 5.7 | 7.16 |  |  | bc
2015-10-22 07:40 | 5.83 | 7.17 |  |  | dk
2015-10-23 10:18 | 5.83 | 7.18 |  |  | bc
2015-10-24 08:14 | 5.73 | 7.1 |  |  | dk
2015-10-25 08:04 | 5.75 | 7.17 |  |  | dk
2015-10-26 11:30 | 5.8 |  |  |  | bc | 7.34
2015-10-27 10:47 | 5.65 | 7.14 |  |  | dk
2015-10-28 10:01 | 5.69 | 7.2 |  |  | dk
2015-10-29 11:18 | 5.55 | 7.16 |  |  | zn
2015-10-30 07:30 | 5.72 |  |  |  | bc | 7.06
2015-10-31 08:20 | 5.37 | 7.26 |  |  | bc
2015-11-01 07:30 | 5.21 | 7.28 |  |  | bc
2015-11-02 07:24 | 5.19 |  |  |  | bc | 7.12
2015-11-03 10:40 | 5.23 | 7.16 |  |  | zn
2015-11-04 06:55 | 5.12 | 7.04 |  |  | bc |  |  |  | thick slurry in hydrolyzer
2015-11-05 10:10 | 5.19 | 7.06 |  |  | zn
2015-11-06 09:10 | 5.01 | 7.24 |  |  | bc
2015-11-07 09:30 | 4.95 | 7.58 |  |  | zn
2015-11-08 11:18 | 5.17 | 7.29 |  |  | zn
2015-11-09 08:38 | 5.04 | 7.02 |  |  | bc |  |  |  | pre feeding
2015-11-10 09:00 | 5.1 | 7.09 |  |  | zn |  |  |  | post feeding
2015-11-11 08:46 | 5.17 | 7.02 |  |  | bc |  |  |  | pre feeding
2015-11-12 12:10 | 5.35 | 7.17 |  |  | zn |  |  |  | post feeding
2015-11-13 08:41 | 5.11 | 7.01 |  |  | bc |  |  |  | pre feeding
2015-11-14 09:30 | 5.04 | 6.98 |  |  | bc
2015-11-15 | 5.17 | 7.1 |  |  | bc |  |  |  | pre feeding
2015-11-16 08:42 | 5.38 | 7.08 |  | 3.84 | zn |  |  |  | during feeding
2015-11-17 08:35 | 5.48 | 7.05 |  |  | zn
2015-11-18 09:20 | 5.58 | 7.18 |  |  | bc |  |  |  | pre feeding
2015-11-19 09:35 | 5.53 | 7.37 |  |  | zn
2015-11-20 10:44 | 5.56 | 7 |  |  | bc |  |  |  | post feeding
2015-11-21 08:00 | 5.34 | 7.06 |  |  | zn |  |  |  | pre feeding
2015-11-22 08:10 | 5.4 | 7.12 |  |  | zn |  |  |  | pre feeding
2015-11-23 08:39 | 5.55 | 7.03 |  |  | bc |  |  |  | pre feeding
2015-11-24 08:15 | 5.56 | 7.11 |  |  | zn |  |  |  | post feeding
2015-11-25 10:00 | 5.45 | 7.02 |  |  | bc |  |  |  | post feeding
2015-11-26 08:05 | 5.6 | 7.18 |  |  | dk |  |  |  | pre feeding
2015-11-27 07:55 | 5.57 | 7.05 |  |  | bc |  |  |  | pre feeding
2015-11-28 10:05 | 5.45 | 7.23 |  |  | dk |  |  |  | post feeding
2015-11-29 10:00 | 5.48 | 7.12 |  |  | dk
2015-11-30 08:25 | 5.25 | 7.07 |  |  | bc |  |  |  | pre feeding
2015-12-01 08:20 | 5.21 | 7.1 |  |  | zn |  |  |  | pre feeding
2015-12-02 07:45 | 4.99 | 7.04 |  |  | bc |  |  |  | pre feeding
2015-12-03 08:30 | 5.07 | 7.12 |  |  | zn |  |  |  | pre feeding
2015-12-04 10:06 | 5.07 | 7.13 |  |  | bc |  |  |  | pre feeding
2015-12-05 08:20 | 4.97 | 7.15 |  |  | zn |  |  |  | pre feeding
2015-12-06 08:05 | 4.99 | 7.04 |  |  | zn |  |  |  | pre feeding
2015-12-07 08:30 | 5.08 | 7.07 |  |  | bc |  |  |  | pre feeding
2015-12-08 08:20 | 5.01 | 7.14 |  |  | zn |  |  |  | pre feeding
2015-12-09 09:47 | 4.93 | 7.15 |  |  | bc |  |  |  | post feeding. Hydrolyzate thicker than usual
2015-12-10 11:00 | 4.78 | 7.1 |  |  | zn |  |  |  | post feeding
2015-12-11 07:45 | 4.68 | 7.13 |  |  | bc |  |  |  | pre feeding
2015-12-12 07:42 | 4.72 | 7.1 |  |  | bc |  |  |  | pre feeding
2015-12-13 07:42 | 4.7 | 7.04 |  |  | bc |  |  |  | pre feeding
2015-12-14 07:42 | 4.7 | 7.01 |  |  | bc |  |  |  | pre feeding
2015-12-15 08:30 | 4.84 | 7.13 |  |  | zn |  |  |  | pre feeding

## tank log
[5 empty] | gallons | gallons
date | time | tank # | what | hauler | amount in | amount out | % full | notes | 1% is approximately 85 gallons when above 47% (in straight sided section of tank)
2015-01-07 | 8:00 | 2 | glycerol |  |  |  | 11 |  | tank #2 500 gallons = 190 seconds pump #1
2015-01-08 | 2:00 | 2 | glycerol |  |  |  | 0 | mostly added yesterday 1% today
2015-01-09 | 8:45 | 2 | glycerol / water | freebird | 4800 |  | 68
2015-01-09 | 9:30 | 2 | glycerol |  |  | 500 | 62 | 190 seconds pump #1
2015-01-12 | 9:15 | 2 | glycerol |  |  | 500 | 56 | 190 sec
2015-01-13 | 9:30 | 2 | glycerol |  |  | 500 | 50 | 190 sec
2015-01-14 11:00 |  | 2 | glycerol |  |  | 500 | 44 | 190
2015-01-15 09:00 |  | 2 | glycerol |  |  | 500 | 38 | 190 sec
2015-01-16 09:30 |  | 1 | glycerol/crumb 1:1 | freebird | 5000 |  | 74
2015-01-26 14:00 |  | 2 | glycerol |  |  | 1870 | 12
2015-01-26 14:00 |  | 1 | glycerol |  | 1870 |  | 96
2015-01-29 10:00 |  | 2 | glycerol/crumb 1:1 | freebird | 5000 |  | 81

## % solids
date | sample | pH | dish # | dish g | wet + dish | dry + dish | % solid
2014-06-04 | digester bottom, pipe |  | 28 | 0 | 645.9 | 103.1 | 15.9622
2014-06-04 | digester sample spout |  | 22 | 0 | 751.4 | 44.9 | 5.9755
2014-06-04 | heifer manure |  | 7 | 0 | 383.4 | 78.1 | 20.3704
2014-06-04 | hydrolizer bottom pipe |  | 76 | 0 | 443.8 | 59.2 | 13.3393
2014-06-04 | hydrolizer puddle |  | 26 | 0 | 380.6 | 74.7 | 19.6269
2014-06-10 | seperated solids |  | 35 | 0 | 99.5 | 31.7 | 31.8593
2014-06-13 | manure pit vtc |  | 15 | 0 | 213.4 | 18.5 | 8.6692
2014-06-13 | goat bedding long hay |  | 36 | 0 | 239.2 | 70.8 | 29.5987
2014-06-13 | prep tank |  | 30 | 0 | 348.4 | 30.8 | 8.8404
2014-06-13 | liquid manure |  | 28 | 0 | 374.5 | 26.6 | 7.1028
2014-06-17 | digestate |  | 22 | 0 | 289.4 | 16.4 | 5.6669
2014-06-17 | manure pit vtc |  | 38 | 0 | 387.6 | 35.4 | 9.1331
2014-06-18 | VTC reception pit | 7 | 26 | 174.6 | 610.6 | 210.1 | 8.1422
2014-06-18 | Alchamist beer waste, round tank | 4.5 | 7 | 179.3 | 526.9 | 195.7 | 4.7181
2014-06-18 | Alchamist, square tank | 4.7 | 76 | 160.4 | 534.7 | 239.9 | 21.2396
2014-06-19 | chopped energy grass VTC |  | 36 | 171.2 | 275.1 | 214.6 | 41.7709
2014-06-19 | chopped reed canary grass |  | 6 | 167.5 | 264.5 | 208.1 | 41.8557
2014-06-23 | manure scrapings VTC | 7.57 | 26 | 174.4 | 581.2 | 228.1 | 13.2006
2014-06-23 | Osha pit | 7.17 | 36 | 171.2 | 853.3 | 214.7 | 6.3774
2014-06-24 | VTC reception pit | 6.88 | 38 | 185.1 | 553.5 | 217.7 | 8.8491
2014-06-30 | VTC reception pit | 6.64 | 38 | 185.2 | 507.8 | 208.7 | 7.2846
2014-07-03 | VTC reception pit | 6.71 | 6 | 167.5 | 698.4 | 215.7 | 9.0789
2014-07-03 | chopped grass VTC |  | 3 | 185.9 | 330.5 | 232.2 | 32.0194
2014-07-03 | ds | 7.37 | 26 | 174.5 | 586.3 | 204.2 | 7.2122
2014-07-03 | Osha pit | 7.5 | 36 | 171.1 | 721.9 | 195.6 | 4.4481
2014-07-15 | prep pit | 7.35 | 2 | 183.7 | 582.1 | 216.1 | 8.1325
2014-07-17 | VTC reception pit |  | 35 | 195.6 | 600.5 | 236 | 9.9778
2014-07-18 | prep pit super thick | 6.82 | 22 | 202.9 | 711.6 | 244.4 | 8.158
2014-07-19 | dimmick grease trap | 6.29 | 14 | 186.1 | 407.6 | 191 | 2.2122
2014-07-21 | seperated liquid digestate | 7.72 | 76 | 160.5 | 405.8 | 166.6 | 2.4868
2014-07-21 | seperated solids |  | 69 | 159.1 | 254.2 | 190.2 | 32.7024
2014-07-21 | heifer manure |  | 33 | 183.3 | 313.7 | 217.5 | 26.227
2014-07-22 | VTC reception pit |  | 26 | 174.5 | 614.4 | 223 | 11.0252
2014-08-20 | Blackbear dewatered remains |  | 74 | 24.84 | 66.76 | 33.78 | 21.3263
2014-08-26 | seperated solids |  | 33 | 25.28 | 61.19 | 36.9 | 32.3587
2014-08-26 | seperated solids |  | 41 | 24.99 | 59.73 | 36.42 | 32.9016
2014-08-26 | seperated solids |  | 120 | 25.21 | 60.3 | 36.68 | 32.6874
2014-09-05 | effluent | 7.58 | 8 | 189.6 | 514.7 | 213.2 | 7.2593
2014-09-05 | effluent | 7.58 | 35 | 195.6 | 593.9 | 226.7 | 7.8082
2014-09-05 | effluent | 7.58 | 33 | 183.3 | 568.3 | 211.8 | 7.4026
2014-09-09 | seperated solids |  | 38 | 185.4 | 352.5 | 240.1 | 32.7349
2014-09-09 | seperated solids |  | 2 | 183.7 | 355.2 | 239.5 | 32.5364
2014-09-09 | seperated solids |  | 15 | 187.9 | 338.2 | 236.8 | 32.5349
2014-09-12 | reese glycerol | 2.7 | 30 | 185.2 | 596.6 | 427.1 | 58.7992
2014-09-12 | reese glycerol | 2.7 | 28 | 187.3 | 583.3 | 417.1 | 58.0303
2014-09-12 | reese glycerol | 2.7 | 23A | 172.1 | 616 | 423.7 | 56.6794
2014-09-17 | seperated solids |  | 38 | 185.3 | 348.4 | 236.8 | 31.5757
2014-09-17 | seperated solids |  | 2 | 183.7 | 351 | 236.4 | 31.5003
2014-09-17 | seperated solids |  | 15 | 187.8 | 368 | 244.9 | 31.687
2014-10-28 | hydrolyzer | 6.54 | 10 | 194.3 | 479 | 216.2 | 7.6923
2014-10-28 | hydrolyzer | 6.54 | 102 | 163.4 | 532.1 | 191.5 | 7.6214
2014-10-28 | hydrolyzer | 6.54 | 39 | 182.6 | 637.6 | 219.7 | 8.1538
2014-10-28 | digester | 7.57 | 19 | 172.4 | 469.5 | 190.5 | 6.0922
2014-10-28 | digester | 7.57 | 32 | 183.6 | 496.4 | 202.8 | 6.1381
2014-10-28 | digester | 7.57 | 21 | 251.6 | 590.2
2014-10-28 | seperated solids |  | 69 | 159.2 | 276.3 | 198.1 | 33.2195
2014-10-28 | seperated solids |  | 3 | 186 | 295.3 | 222.1 | 33.0284
2014-10-28 | seperated solids |  | 18 | 182.2 | 281.9 | 215 | 32.8987
2014-11-26 | hydrolyzer | 7.05 | 30 | 185.2 | 404.4 | 198.3 | 5.9763
2014-11-26 | hydrolyzer | 7.05 | 28 | 187.2 | 400.2 | 200.4 | 6.1972
2014-11-26 | hydrolyzer | 7.05 | 23A | 172.1 | 404 | 186.5 | 6.2096
2014-11-26 | digester | 7.67 | 69 | 159.1 | 390.6 | 177.2 | 7.8186
2014-11-26 | digester | 7.67 | 3 | 186 | 396.1 | 202.9 | 8.0438
2014-11-26 | digester | 7.67 | 18 | 182.4 | 439 | 203.5 | 8.2229
2014-12-11 | prep pit |  | 11 | 193 | 391.5 | 207.4 | 7.2544
2014-12-11 | prep pit |  | 30 | 185.1 | 484.7 | 206.8 | 7.243
2014-12-11 | prep pit |  | 23A | 172.2 | 400.5 | 188.8 | 7.2711
2014-12-11 | hydrolyzer |  | 28 | 187.2 | 391 | 198.5 | 5.5447
2014-12-11 | hydrolyzer |  | 18 | 182.2 | 432.7 | 195.9 | 5.4691
2014-12-11 | hydrolyzer |  | 3 | 186 | 430.3 | 199.8 | 5.6488
2014-12-11 | digester BOT |  | 69 | 159.1 | 301.5 | 169.1 | 7.0225
2014-12-11 | digester BOT |  | 93 | 163.6 | 409.1 | 181.5 | 7.2912
2014-12-11 | digester BOT |  | 32 | 183.7 | 500 | 209.7 | 8.22
2014-12-11 | digester Sep |  | 21 | 251.5 | 468.4 | 264.5 | 5.9935
2014-12-11 | digester Sep |  | 39 | 182.7 | 417.1 | 196.4 | 5.8447
2014-12-11 | digester Sep |  | 10 | 194.2 | 473.9 | 211.8 | 6.2925
2014-12-11 | effluent 1 |  | 19 | 172.4 | 471.1 | 184.4 | 4.0174
2014-12-11 | effluent 1 |  | 102 | 163.4 | 453.3 | 175.2 | 4.0704
2014-12-11 | effluent 2 |  | 37 | 192 | 392.6 | 198.5 | 3.2403
2014-12-11 | effluent 2 |  | 14 | 186.1 | 431.5 | 194 | 3.2192
2014-12-11 | effluent 2 |  | 76 | 160.5 | 420.3 | 169 | 3.2717

## TS VS
date into 150 | sample location | collection date | dish # | sample volume mL | dish wt | dish + wet | dish + dry | dish + ash | date into 550 | % total solids | % fixed solids | % volatile solids | TS g/L standard methods | FS g/L sm | VS g/L sm | TS g/L cornell | FS g/L c | VS g/L c | notes
2015-03-31 14:00 | pp | 2015-03-26 09:50 | 3 |  | 91.02 | 154.32 | 99.24 | 91.94 | 2015-04-02 17:50 | 12.9858 | 11.1922 | 88.8078 |  |  |  | 129.8578 | 14.534 | 115.3239
2015-03-31 14:00 | pp | 2015-03-27 12:00 | 4 |  | 99.75 | 155.4 | 103.97 | 100.24 | 2015-04-02 15:41 | 7.5831 | 11.6114 | 88.3886 |  |  |  | 75.8311 | 8.805 | 67.0261
2015-03-31 14:00 | pp | 2015-03-27 15:45 | 8 |  | 127.74 | 184.04 | 133.47 | 128.25 | 2015-04-02 17:50 | 10.1776 | 8.9005 | 91.0995 |  |  |  | 101.7762 | 9.0586 | 92.7176
2015-03-31 14:00 | pp | 2015-03-27 08:50 | 7 |  | 132.96 | 194.85 | 138.66 | 133.59 | 2015-04-02 15:41 | 9.2099 | 11.0526 | 88.9474 |  |  |  | 92.0989 | 10.1794 | 81.9195
2015-03-31 14:00 | pp | 2015-03-30 15:00 | 2 |  | 98.2 | 134.88 | 101.92 | 98.44 | 2015-04-02 17:50 | 10.1418 | 6.4516 | 93.5484 |  |  |  | 101.4177 | 6.5431 | 94.8746
2015-03-31 14:00 | pp | 2015-03-31 10:00 | 6 |  | 98.57 | 158.21 | 104.91 | 99.43 | 2015-04-02 17:50 | 10.6304 | 13.5647 | 86.4353 |  |  |  | 106.3045 | 14.4199 | 91.8846 |  | %VS as %TS | %VS remaining | % VS destroyed
2015-05-19 | pp | 2015-04-19 | 7 |  | 127.74 | 364.95 | 145.43 | 131.01 | 2015-05-21 | 7.4575 | 18.485 | 81.515 |  |  |  | 74.5753 | 13.7853 | 60.79 |  | 6.079 | 100 | 0
2015-05-19 | h | 2015-04-19 | 8 |  | 132.68 | 318.17 | 145.33 | 135.1 | 2015-05-21 | 6.8198 | 19.1304 | 80.8696 |  |  |  | 68.1977 | 13.0465 | 55.1512 |  | 5.5151 | 90.7241 | 9.2759
2015-05-19 | ds | 2015-04-19 | 9 |  | 133.87 | 319.8 | 143.51 | 136.39 | 2015-05-21 | 5.1847 | 26.1411 | 73.8589 |  |  |  | 51.8475 | 13.5535 | 38.294 |  | 3.8294 | 62.9939 | 37.0061
2015-05-19 | e1 | 2015-04-19 | 10 |  | 133.02 | 328.58 | 140.46 | 135.62 | 2015-05-21 | 3.8045 | 34.9462 | 65.0538 |  |  |  | 38.0446 | 13.2952 | 24.7494 |  | 2.4749 | 40.713 | 59.287
2015-05-19 | ss | 2015-04-19 | 11 |  | 91.07 | 143.03 | 109.04 | 93.04 | 2015-05-21 | 34.5843 | 10.9627 | 89.0373 |  |  |  | 345.843 | 37.9138 | 307.9292 |  | 30.7929 | 506.5456 | -406.5456
2015-05-18 | pp | 2015-05-18 | 1 |  | 133.14 | 364.25 | 158.55 | 137.38 | 2015-05-21 | 10.9948 | 16.6863 | 83.3137 |  |  |  | 109.9476 | 18.3462 | 91.6014 |  | 9.1601 | 100 | 0
2015-05-18 | h | 2015-05-18 | 2 |  | 132.53 | 343 | 149.57 | 135.6 | 2015-05-21 | 8.0962 | 18.0164 | 81.9836 |  |  |  | 80.9617 | 14.5864 | 66.3753 |  | 6.6375 | 72.461 | 27.539
2015-05-18 | ds | 2015-05-18 | 3 |  | 131.01 | 340.45 | 141.06 | 133.81 | 2015-05-21 | 4.7985 | 27.8607 | 72.1393 |  |  |  | 47.9851 | 13.369 | 34.6161 |  | 3.4616 | 37.7899 | 62.2101
2015-05-18 | e1 | 2015-05-18 | 4 |  | 131.04 | 338.95 | 138.6 | 133.58 | 2015-05-21 | 3.6362 | 33.5979 | 66.4021 |  |  |  | 36.3619 | 12.2168 | 24.1451 |  | 2.4145 | 26.3588 | 73.6412
2015-05-18 | e2 | 2015-05-18 | 5 |  | 134.38 | 348.06 | 141.53 | 136.94 | 2015-05-21 | 3.3461 | 35.8042 | 64.1958 |  |  |  | 33.4613 | 11.9805 | 21.4807 |  | 2.1481 | 23.4502 | 76.5498
2015-05-18 | ss | 2015-05-18 | 6 |  | 133.27 | 217.2 | 165.39 | 136.7 | 2015-05-21 | 38.27 | 10.6787 | 89.3213 |  |  |  | 382.6999 | 40.8674 | 341.8325 |  | 34.1832 | 373.1739 | -273.1739
2015-06-16 | pp | 2015-06-16 | 1 | 200 | 134.39 | 329.55 | 145.18 | 136.35 | 2015-06-19 | 5.5288 | 18.165 | 81.835 | 53.95 | 9.8 | 44.15 | 55.288 | 10.043 | 45.2449 |  | 4.5245
2015-06-16 | pp | 2015-06-16 | 2 | 200 | 131.05 | 325.08 | 141.69 | 133.08 | 2015-06-19 | 5.4837 | 19.0789 | 80.9211 | 53.2 | 10.15 | 43.05 | 54.8369 | 10.4623 | 44.3746
2015-06-16 | pp | 2015-06-16 | 3 | 200 | 133.28 | 326.29 | 144.09 | 135.28 | 2015-06-22 | 5.6007 | 18.5014 | 81.4986 | 54.05 | 10 | 44.05 | 56.0075 | 10.3622 | 45.6453
2015-06-16 | h | 2015-06-16 | 4 | 200 | 131 | 328.67 | 142.93 | 133.46 | 2015-06-19 | 6.0353 | 20.6203 | 79.3797 | 59.65 | 12.3 | 47.35 | 60.3531 | 12.445 | 47.9081
2015-06-16 | h | 2015-06-16 | 5 | 200 | 127.73 | 323.47 | 139.71 | 130.23 | 2015-06-19 | 6.1204 | 20.8681 | 79.1319 | 59.9 | 12.5 | 47.4 | 61.2036 | 12.772 | 48.4316
2015-06-16 | h | 2015-06-16 | 6 | 200 | 132.67 | 325.89 | 144.51 | 135.11 | 2015-06-22 | 6.1277 | 20.6081 | 79.3919 | 59.2 | 12.2 | 47 | 61.2773 | 12.6281 | 48.6492
2015-06-16 | ds | 2015-06-16 | 7 | 200 | 132.53 | 332.18 | 145.65 | 136.23 | 2015-06-19 | 6.5715 | 28.2012 | 71.7988 | 65.6 | 18.5 | 47.1 | 65.715 | 18.5324 | 47.1826
2015-06-16 | ds | 2015-06-16 | 8 | 200 | 133.12 | 330.68 | 145.78 | 136.84 | 2015-06-19 | 6.4082 | 29.3839 | 70.6161 | 63.3 | 18.6 | 44.7 | 64.0818 | 18.8297 | 45.2521
2015-06-16 | ds | 2015-06-16 | 9 | 200 | 133.85 | 329.73 | 146.5 | 137.52 | 2015-06-22 | 6.458 | 29.0119 | 70.9881 | 63.25 | 18.35 | 44.9 | 64.5804 | 18.736 | 45.8444
2015-07-30 | ss | 2015-07-30 | 1 | 200 | 180.62 | 245.64 | 203.52 |  |  | 35.2199 |  |  | 114.5 |  |  | 352.1993
2015-07-30 | ss | 2015-07-30 | 2 | 200 | 228.57 | 292.82 | 250.44 | 232.72 | 2015-08-04 | 34.0389 | 18.9758 | 81.0242 | 109.35 | 20.75 | 88.6 | 340.3891 | 64.5914 | 275.7977 | samples ashed on 8/4 and 8/5 were heated over flame until end of visible smoke before going into furnace
2015-07-30 | ss | 2015-07-30 | 3 | 100 | 95.09 | 133.69 | 108.34 | 96.73 | 2015-08-05 | 34.3264 | 12.3774 | 87.6226 | 132.5 | 16.4 | 116.1 | 343.2642 | 42.487 | 300.7772
2015-07-30 | pp | 2015-07-25 | 4 | 200 | 133.24 | 332.73 | 144.3 | 135.54 | 2015-08-05 | 5.5441 | 20.7957 | 79.2043 | 55.3 | 11.5 | 43.8 | 55.4414 | 11.5294 | 43.912 | pp | 50.7083
2015-07-30 | pp | 2015-07-25 | 5 | 100 | 98.62 | 196.61 | 104.09 | 99.69 | 2015-08-04 | 5.5822 | 19.5612 | 80.4388 | 54.7 | 10.7 | 44 | 55.822 | 10.9195 | 44.9025 | h | 36.3667
2015-07-30 | pp | 2015-07-25 | 6 | 100 | 99.8 | 200.09 | 105.65 | 100.95 | 2015-08-05 | 5.8331 | 19.6581 | 80.3419 | 58.5 | 11.5 | 47 | 58.3308 | 11.4667 | 46.8641 | ds | 25.8 | 0.50879
2015-07-30 | pp | 2015-07-27 | 7 | 200 | 132.66 | 328.97 | 146.56 | 135.51 | 2015-08-05 | 7.0806 | 20.5036 | 79.4964 | 69.5 | 14.25 | 55.25 | 70.8064 | 14.5179 | 56.2885
2015-07-30 | pp | 2015-07-27 | 8 | 100 | 98.22 | 200.17 | 105.84 | 99.67 | 2015-08-04 | 7.4743 | 19.0289 | 80.9711 | 76.2 | 14.5 | 61.7 | 74.7425 | 14.2227 | 60.5199
2015-07-30 | pp | 2015-07-27 | 9 | 100 | 97.1 | 194.44 | 104.19 | 98.94 | 2015-08-05 | 7.2837 | 25.952 | 74.048 | 70.9 | 18.4 | 52.5 | 72.8375 | 18.9028 | 53.9347
2015-07-30 | h | 2015-07-30 | 10 | 200 | 131.03 | 325.07 | 140.7 | 133.5 | 2015-08-05 | 4.9835 | 25.5429 | 74.4571 | 48.35 | 12.35 | 36 | 49.8351 | 12.7293 | 37.1058
2015-07-30 | h | 2015-07-30 | 11 | 200 | 133.14 | 327.04 | 142.89 | 135.59 | 2015-08-05 | 5.0284 | 25.1282 | 74.8718 | 48.75 | 12.25 | 36.5 | 50.2837 | 12.6354 | 37.6483
2015-07-30 | h | 2015-07-30 | 12 | 100 | 90.22 | 188.38 | 95.1 | 91.44 | 2015-08-04 | 4.9715 | 25 | 75 | 48.8 | 12.2 | 36.6 | 49.7148 | 12.4287 | 37.2861
2015-07-30 | ds | 2015-07-30 | 13 | 200 | 134.38 | 333.7 | 142.2 | 137.02 | 2015-08-05 | 3.9233 | 33.7596 | 66.2404 | 39.1 | 13.2 | 25.9 | 39.2334 | 13.245 | 25.9884
2015-07-30 | ds | 2015-07-30 | 14 | 200 | 127.73 | 321.18 | 135.37 | 130.31 | 2015-08-05 | 3.9493 | 33.7696 | 66.2304 | 38.2 | 12.9 | 25.3 | 39.4934 | 13.3368 | 26.1566
2015-07-30 | ds | 2015-07-30 | 15 | 200 | 131.01 | 328.58 | 138.87 | 133.63 | 2015-08-04 | 3.9783 | 33.3333 | 66.6667 | 39.3 | 13.1 | 26.2 | 39.7834 | 13.2611 | 26.5222
2015-07-30 | e1 | 2015-07-30 | 16 | 200 | 132.54 | 331.12 | 138.92 | 135.01 | 2015-08-05 | 3.2128 | 38.7147 | 61.2853 | 31.9 | 12.35 | 19.55 | 32.1281 | 12.4383 | 19.6898
2015-07-30 | e1 | 2015-07-30 | 17 | 200 | 133.85 | 328.71 | 140.08 | 136.27 | 2015-08-05 | 3.1972 | 38.8443 | 61.1557 | 31.15 | 12.1 | 19.05 | 31.9717 | 12.4192 | 19.5525
2015-07-30 | e1 | 2015-07-30 | 18 | 100 | 91.13 | 188.24 | 94.25 | 92.32 | 2015-08-05 | 3.2129 | 38.141 | 61.859 | 31.2 | 11.9 | 19.3 | 32.1285 | 12.2541 | 19.8744
2015-11-19 | slime | 2015-11-19 | 1 | 200 | 132.53 | 342.23 | 153.91 |  |  | 10.1955 |  |  | 106.9 |  |  | 101.9552
2015-11-19 | slime | 2015-11-19 | 2 | 200 | 132.67 | 330.38 | 152.3 |  |  | 9.9287 |  |  | 98.15 |  |  | 99.2868
2015-11-19 | slime | 2015-11-19 | 3 | 200 | 131.03 | 331.2 | 151.23 |  |  | 10.0914 |  |  | 101 |  |  | 100.9142

## Alkalinity
date collected | sample location | sample volume mL | H2SO4 N | pH initial | H2SO4 Vi ml | H2SO4 Vf at pH 5.75 | H2SO4 Vf at pH 4.3 | H2SO4 Vf at pH 4.0 | mL V 5.75 | mL V 4.3 | mL V 4.0 | TA | PA 5.75 | IA 4.3 | ripley ratio IA:PA | initials | notes
2014-11-12 | h | 50 | 0.25 | 6.62 | 2.4 | 8.1 | 38.2 | 42.9 | 5.7 | 30.1 | 4.7 | 10125 | 1425 | 7525 | 5.2807
2014-11-12 | Digester | 50 | 0.25 | 8.16 | 8.7 | 45.5 | 52.4 | 53.9 | 36.8 | 6.9 | 1.5 | 11300 | 9200 | 1725 | 0.1875 |  | very foamy
2014-11-25 | pp | 50 | 0.25 | 6.69 | 0.5 | 18.1 | 37.4 | 39.7 | 17.6 | 19.3 | 2.3 | 9800 | 4400 | 4825 | 1.0966
2014-11-25 | h | 50 | 0.25 | 6.52 | 2.6 | 8.2 | 38 | 41.2 | 5.6 | 29.8 | 3.2 | 9650 | 1400 | 7450 | 5.3214
2014-11-26 | h | 50 | 0.25 | 7.1 | 1.2 | 18.5 | 38.9 | 44.1 | 17.3 | 20.4 | 5.2 | 10725 | 4325 | 5100 | 1.1792
2014-11-26 | Digester | 50 | 0.25 | 7.74 | 0 | 37.5 | 47.95 | 48.6 | 37.5 | 10.45 | 0.65 | 12150 | 9375 | 2612.5 | 0.27867
2014-11-28 | h | 50 | 0.25 | 7.02 | 0.5 | 15 | 34.2 | 38.7 | 14.5 | 19.2 | 4.5 | 9550 | 3625 | 4800 | 1.3241
2014-11-28 | Digester | 50 | 0.25 | 8.21 | 0 | 31.9 | 42.8 | 43.9 | 31.9 | 10.9 | 1.1 | 10975 | 7975 | 2725 | 0.34169
2014-12-09 | pp | 50 | 0.25 | 6.64 | 0 | 13.4 | 29.9 | 32.5 | 13.4 | 16.5 | 2.6 | 8125 | 3350 | 4125 | 1.2313
2014-12-09 | h | 50 | 0.25 | 6.91 | 0 | 6.7 | 24.4 | 28 | 6.7 | 17.7 | 3.6 | 7000 | 1675 | 4425 | 2.6418
2014-12-09 | Digester BOT | 50 | 0.25 | 8.17 | 0 | 32.7 | 41.8 | 42.7 | 32.7 | 9.1 | 0.9 | 10675 | 8175 | 2275 | 0.27829
2014-12-09 | ds | 50 | 0.25 | 7.45 | 0 | 30.5 | 43.4 | 44.6 | 30.5 | 12.9 | 1.2 | 11150 | 7625 | 3225 | 0.42295
2014-12-09 | e1 | 50 | 0.25 | 7.73 | 0 | 29.7 | 42.4 | 43.5 | 29.7 | 12.7 | 1.1 | 10875 | 7425 | 3175 | 0.42761
2014-12-09 | e2 | 50 | 0.25 | 8.11 | 0 | 31.6 | 42 | 42.8 | 31.6 | 10.4 | 0.8 | 10700 | 7900 | 2600 | 0.32911
2014-12-24 | h | 50 | 0.25 | 6.32 | 0 | 4.6 | 35.1 | 39.7 | 4.6 | 30.5 | 4.6 | 9925 | 1150 | 7625 | 6.6304 |  | fozen sample, thawed and tested 12-29
2014-12-24 | ds | 50 | 0.25 | 7.9 | 0 | 28.4 | 39.9 | 41.2 | 28.4 | 11.5 | 1.3 | 10300 | 7100 | 2875 | 0.40493 |  | fozen sample, thawed and tested 12-29
2014-12-29 | h | 50 | 0.25 | 6.22 | 0 | 11.2 | 39 | 42.6 | 11.2 | 27.8 | 3.6 | 10650 | 2800 | 6950 | 2.4821
2014-12-29 | ds | 50 | 0.25 | 8.12 | 0 | 34.5 | 44.5 | 45.5 | 34.5 | 10 | 1 | 11375 | 8625 | 2500 | 0.28986
2015-01-05 | h | 50 | 0.25 | 5.84 | 0 | 2.4 | 39.9 | 44.5 | 2.4 | 37.5 | 4.6 | 11125 | 600 | 9375 | 15.625 |  | collected 10 am, tested 4pm
2015-01-05 | ds | 50 | 0.25 | 8.29 | 0 | 38.8 | 44.8 | 46.8 | 38.8 | 6 | 2 | 11700 | 9700 | 1500 | 0.15464 |  | collected 10 am, tested 4pm
2015-01-20 | h | 50 | 0.25 | 6.34 | 0 | 10.5 | 37.3 | 40.5 | 10.5 | 26.8 | 3.2 | 10125 | 2625 | 6700 | 2.5524
2015-01-20 | ds | 50 | 0.25 | 8.32 | 0 | 32.6 | 37.9 | 39.6 | 32.6 | 5.3 | 1.7 | 9900 | 8150 | 1325 | 0.16258 |  | foamed
2015-02-27 15:00 | h | 50 | 0.25 | 5.2 | 0 |  | 17.6 | 22.7 | 0 | 17.6 | 5.1 | 5675 | 0 | 4400
2015-02-27 15:15 | ds | 50 | 0.25 | 7.8 | 0 | 29.7 | 35.9 | 36 | 29.7 | 6.2 | 0.1 | 9000 | 7425 | 1550 | 0.20875 |  | foamed
2015-04-07 | h | 50 | 0.25 | 4.62 | 0 |  | 5.9 | 10.4 | 0 | 5.9 | 4.5 | 2600 | 0 | 1475 |  |  | oily
2015-04-07 | h | 50 | 0.25 | 4.61 | 10.4 |  | 16.3 | 20.9 | 0 | 5.9 | 4.6 | 2625 | 0 | 1475 |  |  | oily
2015-04-07 | h | 50 | 0.25 | 4.61 | 21 |  | 27.2 | 31.3 | 0 | 6.2 | 4.1 | 2575 | 0 | 1550 |  |  | oily
2015-04-07 | ds | 50 | 0.25 | 7.38 | 0 | 15.5 | 22.9 | 24.4 | 15.5 | 7.4 | 1.5 | 6100 | 3875 | 1850 | 0.47742
2015-04-07 | ds | 50 | 0.25 | 7.4 | 0 | 15 | 22.1 | 23.1 | 15 | 7.1 | 1 | 5775 | 3750 | 1775 | 0.47333
2015-04-07 | ds | 50 | 0.25 | 7.41 | 0 | 14.8 | 22.2 | 23.2 | 14.8 | 7.4 | 1 | 5800 | 3700 | 1850 | 0.5
2015-04-10 10:30 | ds | 50 | 0.25 | 7.41 | 0 | 14 | 21.4 | 22.6 | 14 | 7.4 | 1.2 | 5650 | 3500 | 1850 | 0.52857
2015-04-10 10:30 | ds | 50 | 0.25 | 7.42 | 0 | 13.9 | 21.6 | 22.5 | 13.9 | 7.7 | 0.9 | 5625 | 3475 | 1925 | 0.55396
2015-04-10 10:30 | ds | 50 | 0.25 | 7.42 | 0 | 14.4 | 21.5 | 22.7 | 14.4 | 7.1 | 1.2 | 5675 | 3600 | 1775 | 0.49306
2015-04-10 10:30 | e2 | 50 | 0.25 | 7.49 | 0 | 17.5 | 25.2 | 26.2 | 17.5 | 7.7 | 1 | 6550 | 4375 | 1925 | 0.44
2015-04-10 10:30 | e2 | 50 | 0.25 | 7.5 | 0 | 17.2 | 25.1 | 26.5 | 17.2 | 7.9 | 1.4 | 6625 | 4300 | 1975 | 0.4593
2015-04-10 10:30 | e2 | 50 | 0.25 | 7.5 | 0 | 19.2 | 24.8 | 26.6 | 19.2 | 5.6 | 1.8 | 6650 | 4800 | 1400 | 0.29167
2015-04-10 10:30 | h | 50 | 0.25 | 4.58 | 1.7 |  | 6.5 | 11.4 | 0 | 4.8 | 4.9 | 2425 | 0 | 1200
2015-04-10 10:30 | h | 50 | 0.25 | 4.55 | 11.4 |  | 15.9 | 20.7 | 0 | 4.5 | 4.8 | 2325 | 0 | 1125
2015-04-10 10:30 | h | 50 | 0.25 | 4.57 | 20.7 |  | 25.7 | 30.3 | 0 | 5 | 4.6 | 2400 | 0 | 1250
2015-04-13 09:22 | ds | 50 | 0.25 | 7.37 | 0 | 13.9 | 21.2 | 22.8 | 13.9 | 7.3 | 1.6 | 5700 | 3475 | 1825 | 0.52518
2015-04-13 09:22 | ds | 50 | 0.25 | 7.33 | 0 | 14.1 | 20.9 | 22 | 14.1 | 6.8 | 1.1 | 5500 | 3525 | 1700 | 0.48227
2015-04-13 09:22 | ds | 50 | 0.25 | 7.33 | 0 | 13.8 | 20.9 | 21.9 | 13.8 | 7.1 | 1 | 5475 | 3450 | 1775 | 0.51449
2015-04-13 09:22 | h | 50 | 0.25 | 4.57 | 0 |  | 5.4 | 10.3 | 0 | 5.4 | 4.9 | 2575 | 0 | 1350
2015-04-13 09:22 | h | 50 | 0.25 | 4.57 | 10.3 |  | 15.6 | 20.4 | 0 | 5.3 | 4.8 | 2525 | 0 | 1325
2015-04-13 09:22 | h | 50 | 0.25 | 4.6 | 20.4 |  | 26.1 | 30.5 | 0 | 5.7 | 4.4 | 2525 | 0 | 1425
2015-04-17 10:30 | ds | 50 | 0.25 | 7.32 | 0 | 14 | 21.5 | 22.6 | 14 | 7.5 | 1.1 | 5650 | 3500 | 1875 | 0.53571
2015-04-17 10:30 | ds | 50 | 0.25 | 7.39 | 0.1 | 13.7 | 20.7 | 21.8 | 13.6 | 7 | 1.1 | 5425 | 3400 | 1750 | 0.51471
2015-04-17 10:30 | ds | 50 | 0.25 | 7.38 | 0 | 13 | 20.6 | 21.9 | 13 | 7.6 | 1.3 | 5475 | 3250 | 1900 | 0.58462
2015-04-17 10:30 | h | 50 | 0.25 | 4.69 | 0 |  | 7 | 11.4 | 0 | 7 | 4.4 | 2850 | 0 | 1750
2015-04-17 10:30 | h | 50 | 0.25 | 4.7 | 11.4 |  | 18.3 | 22.7 | 0 | 6.9 | 4.4 | 2825 | 0 | 1725
2015-04-17 10:30 | h | 50 | 0.25 | 4.71 | 22.7 |  | 29.9 | 34 | 0 | 7.2 | 4.1 | 2825 | 0 | 1800
2015-04-24 10:45 | ds | 50 | 0.25 | 7.35 | 0 | 13.6 | 21 | 22.2 | 13.6 | 7.4 | 1.2 | 5550 | 3400 | 1850 | 0.54412 |  | 3 hrs between collecting and testing
2015-04-24 10:45 | ds | 50 | 0.25 | 7.35 | 0 | 13.9 | 21.1 | 22.5 | 13.9 | 7.2 | 1.4 | 5625 | 3475 | 1800 | 0.51799
2015-04-24 10:45 | ds | 50 | 0.25 | 7.37 | 0 | 13.7 | 20.8 | 21.9 | 13.7 | 7.1 | 1.1 | 5475 | 3425 | 1775 | 0.51825
2015-04-24 10:45 | h | 50 | 0.25 | 4.7 | 22.2 |  | 28.2 | 32 | 0 | 6 | 3.8 | 2450 | 0 | 1500
2015-04-24 10:45 | h | 50 | 0.25 | 4.68 | 32 |  | 37.7 | 41.6 | 0 | 5.7 | 3.9 | 2400 | 0 | 1425
2015-04-24 10:45 | h | 50 | 0.25 | 4.7 | 26 |  | 31.6 | 35.5 | 0 | 5.6 | 3.9 | 2375 | 0 | 1400
2015-04-21 09:15 | h | 50 | 0.25 | 4.73 | 0.7 |  | 6.9 | 11.3 | 0 | 6.2 | 4.4 | 2650 | 0 | 1550 |  |  | frozen, thawed in double boiler
2015-04-21 09:15 | h | 50 | 0.25 | 4.73 | 11.3 |  | 17.8 | 22.1 | 0 | 6.5 | 4.3 | 2700 | 0 | 1625 |  |  | frozen, thawed in double boiler
2015-04-21 09:15 | h | 50 | 0.25 | 4.72 | 22.1 |  | 30 | 34.1 | 0 | 7.9 | 4.1 | 3000 | 0 | 1975 |  |  | frozen, thawed in double boiler
2015-04-21 09:15 | ds | 50 | 0.25 | 7.59 | 0 | 14.9 | 24.6 | 26.5 | 14.9 | 9.7 | 1.9 | 6625 | 3725 | 2425 | 0.65101 |  | frozen, thawed in double boiler
2015-04-21 09:15 | ds | 50 | 0.25 | 7.58 | 0 | 14.8 | 24 | 25.6 | 14.8 | 9.2 | 1.6 | 6400 | 3700 | 2300 | 0.62162 |  | frozen, thawed in double boiler
2015-04-21 09:15 | ds | 50 | 0.25 | 7.59 | 0 | 15.3 | 24.7 | 26.4 | 15.3 | 9.4 | 1.7 | 6600 | 3825 | 2350 | 0.61438 |  | frozen, thawed in double boiler
2015-05-01 02:00 | ds | 50 | 0.25 | 7.34 | 10 | 27.82 | 34.2 | 35.1 | 17.82 | 6.38 | 0.9 | 6275 | 4455 | 1595 | 0.35802
2015-05-01 02:00 | ds | 50 | 0.25 | 7.34 | 10 | 26.6 | 33.55 | 35.18 | 16.6 | 6.95 | 1.63 | 6295 | 4150 | 1737.5 | 0.41867
2015-05-01 02:00 | ds | 50 | 0.25 | 7.33 | 10 | 26.22 | 33.8 | 35.32 | 16.22 | 7.58 | 1.52 | 6330 | 4055 | 1895 | 0.46732
2015-05-01 02:00 | h | 50 | 0.25 | 4.71 | 11 |  | 15.43 | 18.8 | 0 | 4.43 | 3.37 | 1950 | 0 | 1107.5
2015-05-01 02:00 | h | 50 | 0.25 | 4.71 | 20 |  | 23.7 | 27 | 0 | 3.7 | 3.3 | 1750 | 0 | 925
2015-05-01 02:00 | h | 50 | 0.25 | 4.72 | 27 |  | 31.75 | 35.22 | 0 | 4.75 | 3.47 | 2055 | 0 | 1187.5
2015-05-08 | ds | 50 | 0.25 | 7.27 | 0 | 15.9 | 24.5 | 26.4 | 15.9 | 8.6 | 1.9 | 6600 | 3975 | 2150 | 0.54088
2015-05-08 | ds | 50 | 0.25 | 7.27 | 0 | 15 | 21.4 | 22.2 | 15 | 6.4 | 0.8 | 5550 | 3750 | 1600 | 0.42667
2015-05-08 | ds | 50 | 0.25 | 7.27 | 0 | 15.6 | 23 | 24.4 | 15.6 | 7.4 | 1.4 | 6100 | 3900 | 1850 | 0.47436
2015-05-08 | h | 50 | 0.25 | 4.94 | 0 |  | 6.4 | 9.6 | 0 | 6.4 | 3.2 | 2400 | 0 | 1600
2015-05-08 | h | 50 | 0.25 | 4.94 | 9.6 |  | 16.3 | 19.6 | 0 | 6.7 | 3.3 | 2500 | 0 | 1675
2015-05-08 | h | 50 | 0.25 | 4.94 | 19.7 |  | 26.2 | 29.5 | 0 | 6.5 | 3.3 | 2450 | 0 | 1625
2015-05-15 | ds | 50 | 0.25 | 7.32 | 0 | 15.5 | 23.9 | 25.1 | 15.5 | 8.4 | 1.2 | 6275 | 3875 | 2100 | 0.54194
2015-05-15 | ds | 50 | 0.25 | 7.32 | 0 | 14.7 | 23.5 | 25.1 | 14.7 | 8.8 | 1.6 | 6275 | 3675 | 2200 | 0.59864
2015-05-15 | ds | 50 | 0.25 | 7.34 | 0 | 13.6 | 23.4 | 24.5 | 13.6 | 9.8 | 1.1 | 6125 | 3400 | 2450 | 0.72059
2015-05-15 | ds | 50 | 0.25 | 7.31 | 0 | 14.4 | 22.6 | 24 | 14.4 | 8.2 | 1.4 | 6000 | 3600 | 2050 | 0.56944
2015-05-15 | h | 50 | 0.25 | 5.14 | 24.1 |  | 32 | 35.3 | 0 | 7.9 | 3.3 | 2800 | 0 | 1975
2015-05-15 | h | 50 | 0.25 | 5.14 | 35.3 |  | 43.4 | 46.6 | 0 | 8.1 | 3.2 | 2825 | 0 | 2025
2015-05-15 | h | 50 | 0.25 | 5.14 | 24.6 |  | 32.9 | 36 | 0 | 8.3 | 3.1 | 2850 | 0 | 2075
2015-05-21 | ds | 50 | 0.25 | 7.21 | 0 | 14.4 | 23 | 24.7 | 14.4 | 8.6 | 1.7 | 6175 | 3600 | 2150 | 0.59722
2015-05-21 | ds | 50 | 0.25 | 7.21 | 0 | 13.4 | 22.3 | 24.1 | 13.4 | 8.9 | 1.8 | 6025 | 3350 | 2225 | 0.66418
2015-05-21 | ds | 50 | 0.25 | 7.22 | 0 | 13.7 | 22.6 | 24 | 13.7 | 8.9 | 1.4 | 6000 | 3425 | 2225 | 0.64964 |  | after lunch
2015-05-21 | h | 50 | 0.25 | 5.04 | 0 |  | 6.8 | 9.8 | 0 | 6.8 | 3 | 2450 | 0 | 1700
2015-05-21 | h | 50 | 0.25 | 5.04 | 9.8 |  | 16.9 | 20 | 0 | 7.1 | 3.1 | 2550 | 0 | 1775
2015-05-21 | h | 50 | 0.25 | 5.04 | 20 |  | 26.8 | 29.9 | 0 | 6.8 | 3.1 | 2475 | 0 | 1700
2015-05-29 | ds | 50 | 0.25 | 7.14 | 0 | 11.4 | 20.8 | 22.4 | 11.4 | 9.4 | 1.6 | 5600 | 2850 | 2350 | 0.82456 |  | didn't bounce at 5.75 like it usually does
2015-05-29 | ds | 50 | 0.25 | 7.15 | 0 | 11.4 | 21.1 | 22.8 | 11.4 | 9.7 | 1.7 | 5700 | 2850 | 2425 | 0.85088
2015-05-29 | ds | 50 | 0.25 | 7.15 | 0 | 11.4 | 21 | 22.6 | 11.4 | 9.6 | 1.6 | 5650 | 2850 | 2400 | 0.84211
2015-05-29 | h | 50 | 0.25 | 5.24 | 12.6 |  | 20.5 | 23.3 | 0 | 7.9 | 2.8 | 2675 | 0 | 1975
2015-05-29 | h | 50 | 0.25 | 5.23 | 23.3 |  | 30.9 | 33.8 | 0 | 7.6 | 2.9 | 2625 | 0 | 1900
2015-05-29 | h | 50 | 0.25 | 5.24 | 33.8 |  | 41.8 | 44.8 | 0 | 8 | 3 | 2750 | 0 | 2000
2015-06-04 | h | 50 | 0.25 | 5.02 | 0 |  | 7.87 | 11.55 | 0 | 7.87 | 3.68 | 2887.5 | 0 | 1967.5
2015-06-04 | h | 50 | 0.25 | 5.02 | 12 |  | 19.6 | 23 | 0 | 7.6 | 3.4 | 2750 | 0 | 1900
2015-06-04 | h | 50 | 0.25 | 5.01 | 35 |  | 42.5 | 46.5 | 0 | 7.5 | 4 | 2875 | 0 | 1875
2015-06-04 | ds | 50 | 0.25 | 7.36 | 0 | 11.2 | 20.8 | 22.8 | 11.2 | 9.6 | 2 | 5700 | 2800 | 2400 | 0.85714
2015-06-04 | ds | 50 | 0.25 | 7.11 | 0 | 11.2 | 20.9 | 22.7 | 11.2 | 9.7 | 1.8 | 5675 | 2800 | 2425 | 0.86607
2015-06-04 | ds | 50 | 0.25 | 7.14 | 0 | 11.5 | 21.2 | 23.2 | 11.5 | 9.7 | 2 | 5800 | 2875 | 2425 | 0.84348
2015-06-08 | ds | [13 empty] | 0.77 |  | numbers lost, but had ripley in email
2015-06-08 | ds | [13 empty] | 0.9 |  | numbers lost, but had ripley in email
2015-06-08 | ds | [13 empty] | 0.88 |  | numbers lost, but had ripley in email
2015-06-12 | ds | 50 | 0.25 | 7.17 | 0 | 10.7 | 19.2 | 20.9 | 10.7 | 8.5 | 1.7 | 5225 | 2675 | 2125 | 0.79439
2015-06-12 | ds | 50 | 0.25 | 7.11 | 0 | 10.2 | 19.2 | 20.85 | 10.2 | 9 | 1.65 | 5212.5 | 2550 | 2250 | 0.88235
2015-06-12 | ds | 50 | 0.25 | 7.13 | 0 | 10.9 | 18.7 | 20.4 | 10.9 | 7.8 | 1.7 | 5100 | 2725 | 1950 | 0.7156
2015-06-12 | h | 50 | 0.25 | 4.71 | 0 |  | 3.7 | 7 | 0 | 3.7 | 3.3 | 1750 | 0 | 925
2015-06-12 | h | 50 | 0.25 | 4.72 | 7 |  | 11.2 | 14.1 | 0 | 4.2 | 2.9 | 1775 | 0 | 1050
2015-06-12 | h | 50 | 0.25 | 4.73 | 15 |  | 19 | 22.1 | 0 | 4 | 3.1 | 1775 | 0 | 1000
2015-06-18 | ds | 50 | 0.25 | 7.25 | 0 | 11.1 | 19 | 20.5 | 11.1 | 7.9 | 1.5 | 5125 | 2775 | 1975 | 0.71171
2015-06-18 | ds | 50 | 0.25 | 7.27 | 0 | 10.7 | 19 | 20.9 | 10.7 | 8.3 | 1.9 | 5225 | 2675 | 2075 | 0.7757
2015-06-18 | ds | 50 | 0.25 | 7.29 | 0 | 11 | 18.8 | 20.4 | 11 | 7.8 | 1.6 | 5100 | 2750 | 1950 | 0.70909
2015-06-18 | h | 50 | 0.25 | 5 | 0 |  | 5.9 | 8.8 | 0 | 5.9 | 2.9 | 2200 | 0 | 1475
2015-06-18 | h | 50 | 0.25 | 5.01 | 8.8 |  | 14.8 | 17.8 | 0 | 6 | 3 | 2250 | 0 | 1500
2015-06-18 | h | 50 | 0.25 | 5 | 17.8 |  | 23.6 | 26.7 | 0 | 5.8 | 3.1 | 2225 | 0 | 1450
2015-06-26 | ds | 50 | 0.25 | 7.26 | 0 | 11.3 | 20.1 | 21.6 | 11.3 | 8.8 | 1.5 | 5400 | 2825 | 2200 | 0.77876 |  | before lunch
2015-06-26 | ds | 50 | 0.25 | 7.29 | 0 | 11.7 | 20.4 | 21.9 | 11.7 | 8.7 | 1.5 | 5475 | 2925 | 2175 | 0.74359 |  | after lunch
2015-06-26 | ds | 50 | 0.25 | 7.28 | 0 | 11.5 | 20.3 | 21.8 | 11.5 | 8.8 | 1.5 | 5450 | 2875 | 2200 | 0.76522
2015-06-26 | h | 50 | 0.25 | 5.02 | 0 |  | 6 | 8.8 | 0 | 6 | 2.8 | 2200 | 0 | 1500
2015-06-26 | h | 50 | 0.25 | 5.03 | 8.8 |  | 15.1 | 18 | 0 | 6.3 | 2.9 | 2300 | 0 | 1575
2015-06-26 | h | 50 | 0.25 | 5.03 | 18 |  | 24.5 | 27.7 | 0 | 6.5 | 3.2 | 2425 | 0 | 1625
2015-06-30 | ds | 50 | 0.25 | 7.26 | 0 | 12.2 | 20 | 22.5 | 12.2 | 7.8 | 2.5 | 5625 | 3050 | 1950 | 0.63934
2015-06-30 | ds | 50 | 0.25 | 7.35 | 0 | 12 | 19.5 | 21.3 | 12 | 7.5 | 1.8 | 5325 | 3000 | 1875 | 0.625
2015-06-30 | ds | 50 | 0.25 | 7.36 | 0 | 11.9 | 19.5 | 21.4 | 11.9 | 7.6 | 1.9 | 5350 | 2975 | 1900 | 0.63866
2015-06-30 | h | 50 | 0.25 | 5.43 | 0 |  | 8.5 | 11.4 | 0 | 8.5 | 2.9 | 2850 | 0 | 2125
2015-06-30 | h | 50 | 0.25 | 5.43 | 11.4 |  | 20.1 | 23 | 0 | 8.7 | 2.9 | 2900 | 0 | 2175 |  | zn
2015-06-30 | h | 50 | 0.25 | 5.43 | 23 |  | 31.5 | 34.5 | 0 | 8.5 | 3 | 2875 | 0 | 2125 |  | zn
2015-07-02 | h | 50 | 0.25 | 5.1 | 0 |  | 7.5 | 11.7 | 0 | 7.5 | 4.2 | 2925 | 0 | 1875 |  | bb
2015-07-02 | h | 50 | 0.25 | 5.09 | 20.2 |  | 28.3 | 31.7 | 0 | 8.1 | 3.4 | 2875 | 0 | 2025 |  | bb
2015-07-02 | h | 50 | 0.25 | 5.08 | 31.7 |  | 40.1 | 43.5 | 0 | 8.4 | 3.4 | 2950 | 0 | 2100 |  | bb
2015-07-02 | ds | 50 | 0.25 | 7.33 | 0 | 11.5 | 20.8 | 22.3 | 11.5 | 9.3 | 1.5 | 5575 | 2875 | 2325 | 0.8087 | bb
2015-07-02 | ds | 50 | 0.25 | 7.35 | 0 | 12.2 | 21 | 22.3 | 12.2 | 8.8 | 1.3 | 5575 | 3050 | 2200 | 0.72131 | bb
2015-07-02 | ds | 50 | 0.25 | 7.35 | 0 | 11.7 | 21 | 22.4 | 11.7 | 9.3 | 1.4 | 5600 | 2925 | 2325 | 0.79487 | bb
2015-07-02 | ds | 50 | 0.25 | 7.35 | 0 | 11.5 | 20.5 | 21.6 | 11.5 | 9 | 1.1 | 5400 | 2875 | 2250 | 0.78261 | zn
2015-07-07 | ds | 50 | 0.25 | 7.2 | 0 | 11.6 | 20.7 | 22.2 | 11.6 | 9.1 | 1.5 | 5550 | 2900 | 2275 | 0.78448 | zn
2015-07-07 | ds | 50 | 0.25 | 7.2 | 0 | 12 | 19 | 21 | 12 | 7 | 2 | 5250 | 3000 | 1750 | 0.58333 | zn | from titration curve
2015-07-09 | ds | 50 | 0.25 | 7.26 | 0 | 11 | 20.7 | 22.5 | 11 | 9.7 | 1.8 | 5625 | 2750 | 2425 | 0.88182 | bb
2015-07-09 | ds | 50 | 0.25 | 7.26 | 0 | 11.2 | 20.5 | 22.7 | 11.2 | 9.3 | 2.2 | 5675 | 2800 | 2325 | 0.83036 | bb
2015-07-09 | ds | 50 | 0.25 | 7.26 | 0 | 11.2 | 20.6 | 22.4 | 11.2 | 9.4 | 1.8 | 5600 | 2800 | 2350 | 0.83929 | bb
2015-07-09 | h | 50 | 0.25 | 5.49 | 0 |  | 14 | 18.4 | 0 | 14 | 4.4 | 4600 | 0 | 3500 |  | bb
2015-07-09 | h | 50 | 0.25 | 5.48 | 18.4 |  | 31.9 | 36 | 0 | 13.5 | 4.1 | 4400 | 0 | 3375 |  | bb
2015-07-09 | h | 50 | 0.25 | 5.48 | 0 |  | 13.8 | 17.8 | 0 | 13.8 | 4 | 4450 | 0 | 3450 |  | bb
2015-07-14 | ds | 50 | 0.25 | 7.34 | 0 | 12.2 | 19.8 | 20.7 | 12.2 | 7.6 | 0.9 | 5175 | 3050 | 1900 | 0.62295 | zn
2015-07-14 | ds | 50 | 0.25 | 7.33 | 0 | 12 | 20.1 | 21.3 | 12 | 8.1 | 1.2 | 5325 | 3000 | 2025 | 0.675 | zn
2015-07-14 | ds | 50 | 0.25 | 7.34 | 0 | 12.2 | 19.2 | 20.6 | 12.2 | 7 | 1.4 | 5150 | 3050 | 1750 | 0.57377 | zn | from curve
2015-07-14 | h | 50 | 0.25 | 5.48 | 21.5 |  | 34.3 | 37.6 | 0 | 12.8 | 3.3 | 4025 | 0 | 3200 |  | zn
2015-07-14 | h | 50 | 0.25 | 5.46 | 22.2 |  | 35.7 | 39.3 | 0 | 13.5 | 3.6 | 4275 | 0 | 3375 |  | zn
2015-07-21 | ds | 50 | 0.25 | 7.39 | 0 | 14.5 | 22.4 | 23.9 | 14.5 | 7.9 | 1.5 | 5975 | 3625 | 1975 | 0.54483 | zn | possible misreading of buret at pH 4.3
2015-07-21 | ds | 50 | 0.25 | 7.4 | 0 | 14.6 | 21.6 | 22.9 | 14.6 | 7 | 1.3 | 5725 | 3650 | 1750 | 0.47945 | zn
2015-07-21 | ds | 50 | 0.25 | 7.39 | 0 | 14.5 | 21.5 | 22.7 | 14.5 | 7 | 1.2 | 5675 | 3625 | 1750 | 0.48276 | zn
2015-07-21 | ds | 50 | 0.25 | 7.39 | 0 | 14.5 | 20.5 | 21.5 | 14.5 | 6 | 1 | 5375 | 3625 | 1500 | 0.41379 | zn
2015-07-21 | h | 50 | 0.25 | 5.1 | 17.3 |  | 29.9 | 34.8 | 0 | 12.6 | 4.9 | 4375 | 0 | 3150 |  | zn
2015-07-21 | h | 50 | 0.25 | 5.11 | 34.8 |  | 47.7 |  |  | 12.9 |  |  |  | 3225 |  |  | ran out of acid
2015-07-24 | ds | 50 | 0.21 | 7.37 | 0 | 20.6 | 28.9 | 30.1 | 20.6 | 8.3 | 1.2 | 6321 | 4326 | 1743 | 0.40291 | bb
2015-07-24 | ds | 50 | 0.21 | 7.42 | 0 | 20.5 | 28.4 | 29.4 | 20.5 | 7.9 | 1 | 6174 | 4305 | 1659 | 0.38537 | dr
2015-07-24 | ds | 50 | 0.21 | 7.46 | 0 | 19.4 | 28.8 | 29.3 | 19.4 | 9.4 | 0.5 | 6153 | 4074 | 1974 | 0.48454 | bb
2015-07-24 | h | 50 | 0.21 | 5.15 | 0 |  | 16.2 | 21.8 | 0 | 16.2 | 5.6 | 4578 | 0 | 3402 |  | bb
2015-07-24 | h | 50 | 0.21 | 5.15 | 21.8 |  | 37.9 | 43.6 | 0 | 16.1 | 5.7 | 4578 | 0 | 3381 |  | bb
2015-07-24 | h | 50 | 0.21 | 5.15 | 0 |  | 16.7 | 22.6 | 0 | 16.7 | 5.9 | 4746 | 0 | 3507 |  | bb
2015-07-28 | ds | 50 | 0.21 | 7.45 | 0 | 18.3 | 27.3 |  | 18.3 | 9 |  |  | 3843 | 1890 | 0.4918 | zn | missed 4.0, 28.8 is too far
2015-07-28 | ds | 50 | 0.21 | 7.46 | 0 | 18.2 | 26.7 | 27.2 | 18.2 | 8.5 | 0.5 | 5712 | 3822 | 1785 | 0.46703 | zn
2015-07-28 | ds | 50 | 0.21 | 7.47 | 0 | 19.5 | 27.2 | 28.3 | 19.5 | 7.7 | 1.1 | 5943 | 4095 | 1617 | 0.39487 | zn
2015-07-28 | h | 50 | 0.21 | 5.07 | 0 |  | 16.8 | 23.1 | 0 | 16.8 | 6.3 | 4851 | 0 | 3528 |  | zn
2015-07-30 | ds | 50 | 0.21 | 7.42 | 0 | 21.1 | 29.9 | 31.4 | 21.1 | 8.8 | 1.5 | 6594 | 4431 | 1848 | 0.41706 | bb
2015-07-30 | ds | 50 | 0.21 | 7.43 | 0 | 20.5 | 30 | 31.3 | 20.5 | 9.5 | 1.3 | 6573 | 4305 | 1995 | 0.46341 | bb
2015-07-30 | ds | 50 | 0.21 | 7.45 | 0 | 21.2 | 31.9 | 32.3 | 21.2 | 10.7 | 0.4 | 6783 | 4452 | 2247 | 0.50472 | bb
2015-07-30 | h | 50 | 0.21 | 5.21 | 0 |  | 17.8 | 23.2 | 0 | 17.8 | 5.4 | 4872 | 0 | 3738 |  | bb
2015-07-30 | h | 50 | 0.21 | 5.21 | 23.2 |  | 41.1 | 47.1 | 0 | 17.9 | 6 | 5019 | 0 | 3759 |  | bb
2015-07-30 | h | 50 | 0.21 | 5.21 | 0 |  | 17.9 | 24.3 | 0 | 17.9 | 6.4 | 5103 | 0 | 3759 |  | bb
2015-08-05 | ds | 50 | 0.21 | 7.42 | 0 | 20.7 | 30.2 | 31.7 | 20.7 | 9.5 | 1.5 | 6657 | 4347 | 1995 | 0.45894 | zn
2015-08-05 | ds | 50 | 0.21 | 7.44 | 0 | 21 | 31.3 | 33.5 | 21 | 10.3 | 2.2 | 7035 | 4410 | 2163 | 0.49048 | zn
2015-08-05 | ds | 50 | 0.21 | 7.47 | 0 | 20.9 | 31.2 | 33.2 | 20.9 | 10.3 | 2 | 6972 | 4389 | 2163 | 0.49282 | zn
2015-08-05 | h | 50 | 0.21 | 4.89 | 0 |  | 15.5 | 22.8 | 0 | 15.5 | 7.3 | 4788 | 0 | 3255 |  | zn
2015-08-05 | h | 50 | 0.21 | 4.89 | 22.8 |  | 38.8 | 47.3 | 0 | 16 | 8.5 | 5145 | 0 | 3360 |  | zn
2015-08-05 | h | 50 | 0.21 | 4.89 | 15.7 |  | 31.9 | 40.1 | 0 | 16.2 | 8.2 | 5124 | 0 | 3402 |  | zn
2015-08-11 | ds | 50 | 0.21 | 7.53 | 0 | 22.1 | 31.5 | 33.1 | 22.1 | 9.4 | 1.6 | 6951 | 4641 | 1974 | 0.42534 | zn
2015-08-11 | ds | 50 | 0.21 | 7.53 | 0 | 21.6 | 31.1 | 32.4 | 21.6 | 9.5 | 1.3 | 6804 | 4536 | 1995 | 0.43981 | zn
2015-08-11 | h | 50 | 0.21 | 4.94 | 8 |  | 23.7 | 32 | 0 | 15.7 | 8.3 | 5040 | 0 | 3297 |  | zn
2015-08-11 | h | 50 | 0.21 | 4.94 | 22.5 |  | 38.7 | 47.6 | 0 | 16.2 | 8.9 | 5271 | 0 | 3402 |  | zn
2015-08-17 | ds | 50 | 0.21 | 7.52 | 0 | 20.8 |  |  | 20.8 |  |  |  | 4368 |  |  | zn | oops, 29 is too far
2015-08-17 | ds | 50 | 0.21 | 7.53 | 0 | 21 | 29.4 | 30.5 | 21 | 8.4 | 1.1 | 6405 | 4410 | 1764 | 0.4 | zn
2015-08-17 | ds | 50 | 0.21 | 7.54 | 0 | 21.7 | 30.8 | 32 | 21.7 | 9.1 | 1.2 | 6720 | 4557 | 1911 | 0.41935 | zn
2015-08-17 | h | 50 | 0.21 | 5.04 | 12.4 |  | 29.1 | 35.7 | 0 | 16.7 | 6.6 | 4893 | 0 | 3507 |  | zn
2015-08-17 | h | 50 | 0.21 | 5.03 | 13.3 |  | 30.1 | 36.6 | 0 | 16.8 | 6.5 | 4893 | 0 | 3528 |  | zn
2015-08-24 | ds | 50 | 0.21 | 7.52 | 0.1 | 21.6 | 30.9 | 32 | 21.5 | 9.3 | 1.1 | 6699 | 4515 | 1953 | 0.43256 | zn
2015-08-31 | ds | 50 | 0.25 | 7.43 | 0 | 21 | 32.5 | 33.8 | 21 | 11.5 | 1.3 | 8450 | 5250 | 2875 | 0.54762 | zn | new batch of acid
2015-08-31 | ds | 50 | 0.25 | 7.43 | 7.1 | 29.1 | 40.5 | 41.6 | 22 | 11.4 | 1.1 | 8625 | 5500 | 2850 | 0.51818 | zn
2015-08-31 | h | 50 | 0.25 | 5.07 | 10.9 |  | 27.6 | 34.7 | 0 | 16.7 | 7.1 | 5950 | 0 | 4175 |  | zn
2015-08-31 | h | 50 | 0.25 | 5.08 | 23.3 |  | 40.7 | 47.7 | 0 | 17.4 | 7 | 6100 | 0 | 4350 |  | zn
2015-09-07 | ds | 50 | 0.25 | 7.38 | 0.1 | 17.1 | 27.3 | 28.4 | 17 | 10.2 | 1.1 | 7075 | 4250 | 2550 | 0.6 | zn
2015-09-07 | ds | 50 | 0.25 | 7.41 | 0 | 16.1 | 25.9 | 26.9 | 16.1 | 9.8 | 1 | 6725 | 4025 | 2450 | 0.6087 | zn
2015-09-07 | h | 50 | 0.25 | 5.05 | 5.5 |  | 20.9 | 26.2 | 0 | 15.4 | 5.3 | 5175 | 0 | 3850 |  | zn
2015-09-07 | h | 50 | 0.25 | 5.05 | 7.4 |  | 23.3 | 29.5 | 0 | 15.9 | 6.2 | 5525 | 0 | 3975 |  | zn
2015-09-12 | d (small tank) | 50 | 0.25 | 7.4 | 0 | 15 | 24.3 | 25.4 | 15 | 9.3 | 1.1 | 6350 | 3750 | 2325 | 0.62 | jrh
2015-09-12 | d (small tank) | 50 | 0.25 | 7.4 | 0 | 13.7 | 22.8 | 24.1 | 13.7 | 9.1 | 1.3 | 6025 | 3425 | 2275 | 0.66423 | jrh
2015-09-12 | d (small tank) | 50 | 0.25 | 7.4 | 0 | 13.8 | 22 | 23 | 13.8 | 8.2 | 1 | 5750 | 3450 | 2050 | 0.5942 | jrh
2015-09-12 | h | 50 | 0.25 | 5 | 0 |  | 13.4 | 19.2 | 0 | 13.4 | 5.8 | 4800 | 0 | 3350 |  | jrh
2015-09-12 | h | 50 | 0.25 | 5 | 0 |  | 13 | 19.7 | 0 | 13 | 6.7 | 4925 | 0 | 3250 |  | jrh
2015-09-12 | h | 50 | 0.25 | 5 | 0 |  | 12.7 | 18.8 | 0 | 12.7 | 6.1 | 4700 | 0 | 3175 |  | jrh
2015-09-16 | ds | 50 | 0.25 | 7.34 | 0 | 15.4 | 23.5 | 24.7 | 15.4 | 8.1 | 1.2 | 6175 | 3850 | 2025 | 0.52597 | zn
2015-09-16 | ds | 50 | 0.25 | 7.34 | 0 | 15.8 | 23.3 | 24.6 | 15.8 | 7.5 | 1.3 | 6150 | 3950 | 1875 | 0.47468 | bc
2015-09-16 | h | 50 | 0.25 | 5.04 | 2.9 |  | 18 | 23.4 | 0 | 15.1 | 5.4 | 5125 | 0 | 3775 |  | bc
2015-09-22 | ds | 50 | 0.25 | 7.29 | 0 | 13.9 | 22.8 | 23.6 | 13.9 | 8.9 | 0.8 | 5900 | 3475 | 2225 | 0.64029 | zn
2015-09-22 | ds | 50 | 0.25 | 7.31 | 0.3 | 13.5 | 21.7 | 22.9 | 13.2 | 8.2 | 1.2 | 5650 | 3300 | 2050 | 0.62121 | zn
2015-09-22 | h | 50 | 0.25 | 5.28 | 2.7 |  | 19 | 23.8 | 0 | 16.3 | 4.8 | 5275 | 0 | 4075 |  | zn
2015-09-22 | h | 50 | 0.25 | 5.27 | 22.9 |  | 40 | 45 | 0 | 17.1 | 5 | 5525 | 0 | 4275 |  | zn
2015-10-01 | ds | 50 | 0.25 | 7.41 | 0 | 14.7 | 22.6 | 24.2 | 14.7 | 7.9 | 1.6 | 6050 | 3675 | 1975 | 0.53741 | pb
2015-10-01 | ds | 50 | 0.25 | 7.47 | 9.5 | 23.3 | 31.4 | 33.1 | 13.8 | 8.1 | 1.7 | 5900 | 3450 | 2025 | 0.58696 | jm
2015-10-01 | ds | 50 | 0.25 | 7.46 | 0 | 15 | 22.9 | 24.3 | 15 | 7.9 | 1.4 | 6075 | 3750 | 1975 | 0.52667 | bc
2015-10-01 | h | 50 | 0.25 | 5.05 | 24.3 |  | 39.3 | 45.6 | 0 | 15 | 6.3 | 5325 | 0 | 3750 |  | pb
2015-10-01 | h | 50 | 0.25 | 5.1 | 19.7 |  | 34.5 | 39.8 | 0 | 14.8 | 5.3 | 5025 | 0 | 3700 |  | jm
2015-10-01 | h | 50 | 0.25 | 5.13 | 25.4 |  | 41.1 | 46.6 | 0 | 15.7 | 5.5 | 5300 | 0 | 3925 |  | bc
2015-10-09 | ds | 50 | 0.25 | 7.44 | 0.1 | 15.5 | 23.8 | 25.9 | 15.4 | 8.3 | 2.1 | 6450 | 3850 | 2075 | 0.53896 | zn
2015-10-09 | ds | 50 | 0.25 | 7.44 | 0.5 | 16 | 24 | 25.8 | 15.5 | 8 | 1.8 | 6325 | 3875 | 2000 | 0.51613 | zn | more wood chips and hay bits in sample than usual
2015-10-09 | h | 50 | 0.25 | 5.42 | 13 |  | 30 | 34.2 | 0 | 17 | 4.2 | 5300 | 0 | 4250 |  | zn
2015-10-09 | h | 50 | 0.25 | 5.42 | 17.6 |  | 34.3 | 39.5 | 0 | 16.7 | 5.2 | 5475 | 0 | 4175 |  | zn
2015-10-16 | ds | 50 | 0.25 | 7.53 | 0 | 17.5 | 26 | 28 | 17.5 | 8.5 | 2 | 7000 | 4375 | 2125 | 0.48571 | zn
2015-10-16 | ds | 50 | 0.25 | 7.52 | 0 | 18.2 | 26.3 | 28.1 | 18.2 | 8.1 | 1.8 | 7025 | 4550 | 2025 | 0.44505 | zn
2015-10-16 | h | 50 | 0.25 | 5.77 | 5.4 |  | 26.7 | 31.5 | 0 | 21.3 | 4.8 | 6525 | 0 | 5325 |  | zn
2015-10-16 | h | 50 | 0.25 | 5.77 | 15.6 |  | 36.8 | 42.3 | 0 | 21.2 | 5.5 | 6675 | 0 | 5300 |  | zn
2015-10-27 | ds | 50 | 0.25 | 7.42 | 0 | 20.7 | 29.7 | 31.4 | 20.7 | 9 | 1.7 | 7850 | 5175 | 2250 | 0.43478 | zn | fresh batch of H2SO4
2015-10-27 | ds | 50 | 0.25 | 7.43 | 5.5 | 26.2 | 35.3 | 36.8 | 20.7 | 9.1 | 1.5 | 7825 | 5175 | 2275 | 0.43961 | zn
2015-10-27 | h | 50 | 0.25 | 5.82 | 16.3 |  | 35.3 | 40.2 | 0 | 19 | 4.9 | 5975 | 0 | 4750 |  | zn
2015-10-27 | h | 50 | 0.25 | 5.81 | 14 |  | 34.1 | 38.8 | 0 | 20.1 | 4.7 | 6200 | 0 | 5025 |  | zn
2015-11-05 | ds | 50 | 0.25 | 7.45 | 0.4 | 21.2 | 30.5 | 32.6 | 20.8 | 9.3 | 2.1 | 8050 | 5200 | 2325 | 0.44712 | zn
2015-11-05 | h | 50 | 0.25 | 5.36 | 7.9 |  | 31 | 37.5 | 0 | 23.1 | 6.5 | 7400 | 0 | 5775 |  | zn
2015-11-10 | ds | 50 | 0.25 | 7.42 | 0 | 19.3 | 27.7 | 29.1 | 19.3 | 8.4 | 1.4 | 7275 | 4825 | 2100 | 0.43523 | zn | collected at end of cycle when flow rate very low
2015-11-10 | ds | 50 | 0.25 | 7.38 | 0.9 | 21.1 | 30 | 31.3 | 20.2 | 8.9 | 1.3 | 7600 | 5050 | 2225 | 0.44059 | zn
2015-11-10 | h | 50 | 0.25 | 5.5 | 2.4 |  | 22.1 | 27.9 | 0 | 19.7 | 5.8 | 6375 | 0 | 4925 |  | zn
2015-11-10 | h | 50 | 0.25 | 5.5 | 16.5 |  | 36.5 | 41.8 | 0 | 20 | 5.3 | 6325 | 0 | 5000 |  | zn
2015-11-17 | ds | 50 | 0.25 | 7.5 | 6.1 | 25 | 33.5 | 35.4 | 18.9 | 8.5 | 1.9 | 7325 | 4725 | 2125 | 0.44974 | zn | woodchips in sample
2015-11-17 | ds | 50 | 0.25 | 7.51 | 1.8 | 20.8 | 29.4 | 31.1 | 19 | 8.6 | 1.7 | 7325 | 4750 | 2150 | 0.45263 | zn
2015-11-17 | h | 50 | 0.25 | 5.85 | 0.4 | 2.4 | 22.7 | 27.6 | 2 | 20.3 | 4.9 | 6800 | 500 | 5075 | 10.15 | zn
2015-11-17 | h | 50 | 0.25 | 5.86 | 6.8 | 7.9 | 25.7 | 31 | 1.1 | 17.8 | 5.3 | 6050 | 275 | 4450 | 16.1818 | zn
2015-11-24 | ds | 50 | 0.25 | 7.49 | 1.7 | 22.9 | 32.9 | 34.6 | 21.2 | 10 | 1.7 | 8225 | 5300 | 2500 | 0.4717 | zn
2015-11-24 | ds | 50 | 0.25 | 7.49 | 1.8 | 21.8 | 30.9 | 34.2 | 20 | 9.1 | 3.3 | 8100 | 5000 | 2275 | 0.455 | zn
2015-11-24 | h | 50 | 0.25 | 5.71 | 13.9 |  | 33.4 | 39 | 0 | 19.5 | 5.6 | 6275 | 0 | 4875 |  | zn
2015-11-24 | h | 50 | 0.25 | 5.7 | 15.5 |  | 35.8 | 41.7 | 0 | 20.3 | 5.9 | 6550 | 0 | 5075 |  | zn
2015-12-02 | ds | 50 | 0.25 | 7.51 | 0.4 | 22.9 | 31.4 | 33.2 | 22.5 | 8.5 | 1.8 | 8200 | 5625 | 2125 | 0.37778 | zn
2015-12-02 | ds | 50 | 0.25 | 7.49 | 0.4 | 21.8 | 30.5 | 32 | 21.4 | 8.7 | 1.5 | 7900 | 5350 | 2175 | 0.40654 | zn
2015-12-02 | h | 50 | 0.25 | 5.38 | 2.7 |  | 24.5 | 31.1 | 0 | 21.8 | 6.6 | 7100 | 0 | 5450 |  | zn
2015-12-02 | h | 50 | 0.25 | 5.38 | 6.6 |  | 29 | 35.1 | 0 | 22.4 | 6.1 | 7125 | 0 | 5600 |  | zn
2015-12-11 | ds | 50 | 0.25 | 7.54 | 0.4 | 23.4 | 34 | 35 | 23 | 10.6 | 1 | 8650 | 5750 | 2650 | 0.46087 | zn
2015-12-11 | ds | 50 | 0.25 | 7.55 | 0.9 | 22.7 | 32.7 | 34.3 | 21.8 | 10 | 1.6 | 8350 | 5450 | 2500 | 0.45872 | zn
2015-12-11 | h | 50 | 0.25 | 4.95 | 16.5 |  | 35.5 | 43.8 | 0 | 19 | 8.3 | 6825 | 0 | 4750 |  | zn | hydrolyzer sample thick
2015-12-11 | h | 50 | 0.25 | 4.96 | 17.9 |  | 37.3 | 46.4 | 0 | 19.4 | 9.1 | 7125 | 0 | 4850 |  | zn
2015-12-23 | ds | 50 | 0.25 | 7.46 | 1.9 | 22.5 | 31.5 | 33.2 | 20.6 | 9 | 1.7 | 7825 | 5150 | 2250 | 0.43689 | zn
2015-12-23 | ds | 50 | 0.25 | 7.45 | 0.5 | 20.6 | 29.6 | 31 | 20.1 | 9 | 1.4 | 7625 | 5025 | 2250 | 0.44776 | zn
2015-12-23 | h | 50 | 0.25 | 5.5 | 0.5 |  | 22.9 | 28.2 | 0 | 22.4 | 5.3 | 6925 | 0 | 5600 |  | zn
2015-12-23 | h | 50 | 0.25 | 5.51 | 6.9 |  | 28 | 34.3 | 0 | 21.1 | 6.3 | 6850 | 0 | 5275 |  | zn
2016-01-21 | ds | 50 | 0.25 | 7.59 | 2.2 | 30.2 | 40 | 42.7 | 28 | 9.8 | 2.7 | 10125 | 7000 | 2450 | 0.35 | zn | fresh batch of H2SO4
2016-01-21 | ds | 50 | 0.25 | 7.6 | 2.2 | 29.2 | 39.9 | 42 | 27 | 10.7 | 2.1 | 9950 | 6750 | 2675 | 0.3963 | zn
2016-01-21 | h | 50 | 0.25 | 5.94 | 0.8 | 2.5 | 27.6 | 34.3 | 1.7 | 25.1 | 6.7 | 8375 | 425 | 6275 | 14.7647 | zn
2016-01-21 | h | 50 | 0.25 | 5.92 | 1.8 | 3.6 | 29.2 | 35.2 | 1.8 | 25.6 | 6 | 8350 | 450 | 6400 | 14.2222 | zn
2016-02-04 | ds | 50 | 0.25 | 7.64 | 0.9 | 29.8 | 39 | 40.3 | 28.9 | 9.2 | 1.3 | 9850 | 7225 | 2300 | 0.31834 | zn
2016-02-04 | ds | 50 | 0.25 | 7.65 | 0.9 | 28.7 | 38.8 | 40.3 | 27.8 | 10.1 | 1.5 | 9850 | 6950 | 2525 | 0.36331 | zn
2016-02-04 | h | 50 | 0.25 | 5.5 | 2.9 |  | 26.8 | 33.9 | 0 | 23.9 | 7.1 | 7750 | 0 | 5975 |  | zn
2016-02-04 | h | 50 | 0.25 | 5.48 | 1.6 |  | 25 | 31.6 | 0 | 23.4 | 6.6 | 7500 | 0 | 5850 |  | zn
2016-03-03 | ds | 50 | 0.25 | 7.66 | 1.3 | 28.2 | 38.8 | 41 | 26.9 | 10.6 | 2.2 | 9925 | 6725 | 2650 | 0.39405 | zn | filtered through colander
2016-03-03 | ds | 50 | 0.25 | 7.64 | 0.7 | 25.9 | 36.5 | 38.4 | 25.2 | 10.6 | 1.9 | 9425 | 6300 | 2650 | 0.42063 | zn | unfiltered
2016-03-03 | ds | 50 | 0.25 | 7.65 | 0.4 | 25 | 36.4 | 37.9 | 24.6 | 11.4 | 1.5 | 9375 | 6150 | 2850 | 0.46341 | zn | unfiltered
2016-03-03 | ds | 50 | 0.25 | 7.66 | 0.7 | 26.1 | 37.6 | 37.9 | 25.4 | 11.5 | 0.3 | 9300 | 6350 | 2875 | 0.45276 | zn | filtered through colander
2016-03-03 | h | 50 | 0.25 | 5.52 | 0.5 |  | 20.1 | 25 | 0 | 19.6 | 4.9 | 6125 | 0 | 4900 |  | zn | unfiltered
2016-03-03 | h | 50 | 0.25 | 5.53 | 2.7 |  | 23 | 28.2 | 0 | 20.3 | 5.2 | 6375 | 0 | 5075 |  | zn | filtered through colander
2016-03-03 | h | 50 | 0.25 | 5.52 | 0.5 |  | 21 | 26.1 | 0 | 20.5 | 5.1 | 6400 | 0 | 5125 |  | zn | unfiltered
2016-03-03 | h | 50 | 0.25 | 5.53 | 10.9 |  | 30.8 | 35.9 | 0 | 19.9 | 5.1 | 6250 | 0 | 4975 |  | zn | filtered through colander
2016-04-19 | ds | 50 | 0.25 | 7.58 | 1.5 | 25.7 | 39.15 | 41.25 | 24.2 | 13.45 | 2.1 | 9937.5 | 6050 | 3362.5 | 0.55579 | jrh
2016-04-19 | ds | 50 | 0.25 | 7.55 | 1.2 | 25 | 38 | 39.8 | 23.8 | 13 | 1.8 | 9650 | 5950 | 3250 | 0.54622 | jrh
2016-04-19 | ds | 50 | 0.25 | 7.6 | 0.2 | 23.9 | 36.7 | 39 | 23.7 | 12.8 | 2.3 | 9700 | 5925 | 3200 | 0.54008 | jrh
2016-04-21 | h | 50 | 0.25 | 5.33 | 0 |  | 26.8 | 31 | 0 | 26.8 | 4.2 | 7750 | 0 | 6700 |  | jrh
2016-04-21 | h | 50 | 0.25 | 5.33 | 0 |  | 26 | 30.8 | 0 | 26 | 4.8 | 7700 | 0 | 6500 |  | jrh
2016-07-11 | ds | 50 | 0.25 | 7.51 | 0 | 26.2 | 38.9 | 39.8 | 26.2 | 12.7 | 0.9 | 9950 | 6550 | 3175 | 0.48473 | ph | new batch of acid
2016-07-11 | ds | 50 | 0.25 | 7.56 | 0.4 | 26.8 | 36.9 | 39.3 | 26.4 | 10.1 | 2.4 | 9725 | 6600 | 2525 | 0.38258 | ph
2016-07-11 | ds | 50 | 0.25 | 7.54 | 0.1 | 28.9 | 35.5 | 37.4 | 28.8 | 6.6 | 1.9 | 9325 | 7200 | 1650 | 0.22917 | ph
2016-07-11 | ds | 50 | 0.25 | 7.61 | 0 | 24.2 | 34.8 | 37.3 | 24.2 | 10.6 | 2.5 | 9325 | 6050 | 2650 | 0.43802 | ph
2016-07-11 | ds | 50 | 0.25 | 7.54 | 1.6 | 25.8 | 35.1 | 37.2 | 24.2 | 9.3 | 2.1 | 8900 | 6050 | 2325 | 0.3843 | zn
2016-07-11 | h | 50 | 0.25 | 5.39 | 0 |  | 19.9 | 24.6 |  | 19.9 | 4.7 | 6150 | 0 | 4975 |  | ph
2016-07-11 | h | 50 | 0.25 | 5.4 | 0 |  | 25.8 | 26.6 |  | 25.8 | 0.8 | 6650 | 0 | 6450 |  | ph
2016-07-11 | h | 50 | 0.25 | 5.4 | 0 |  | 19.8 | 24 |  | 19.8 | 4.2 | 6000 | 0 | 4950 |  | ph
2016-07-28 | h | 50 | 0.25 | 4.5 | 1.5 |  | 6.1 | 12.4 |  | 4.6 | 6.3 | 2725 | 0 | 1150 |  | zn
2016-07-28 | h | 50 | 0.25 | 4.47 | 12.4 |  | 16.1 | 23 |  | 3.7 | 6.9 | 2650 | 0 | 925 |  | zn
2016-07-28 | h | 50 | 0.25 | 4.47 | 23 |  | 27 | 33.4 |  | 4 | 6.4 | 2600 | 0 | 1000 |  | zn
2016-07-28 | ds | 50 | 0.25 | 7.3 | 1.5 | 21.3 | 30.9 | 33 | 19.8 | 9.6 | 2.1 | 7875 | 4950 | 2400 | 0.48485 | zn
2016-07-28 | ds | 50 | 0.25 | 7.29 | 1.4 | 21.5 | 31.1 | 33.4 | 20.1 | 9.6 | 2.3 | 8000 | 5025 | 2400 | 0.47761 | zn
2016-08-02 | ds | 50 | 0.25 | 7.34 | 0 | 23.8 | 33.7 | 35.5 | 23.8 | 9.9 | 1.8 | 8875 | 5950 | 2475 | 0.41597 | jrh, dKa
2016-08-02 | ds | 50 | 0.25 | 7.28 | 0 | 23.25 | 34.4 | 36.5 | 23.25 | 11.15 | 2.1 | 9125 | 5812.5 | 2787.5 | 0.47957 | jrh, dKa
2016-08-02 | ds | 50 | 0.25 | 7.29 | 0 | 21.7 | 33.3 | 35.04 | 21.7 | 11.6 | 1.74 | 8760 | 5425 | 2900 | 0.53456 | jrh, dKa
2016-08-02 | h | 50 | 0.25 | 4.89 | 13.9 |  | 24.25 | 29.3 |  | 10.35 | 5.05 | 3850 | 0 | 2587.5 |  | jrh, dKa
2016-09-19 | ds | 50 | 0.25 | 7.4 | 0 | 24.9 | 34.6 | 36.4 | 24.9 | 9.7 | 1.8 | 9100 | 6225 | 2425 | 0.38956 | JRH
2016-09-19 | ds | 50 | 0.25 | 7.36 | 0 | 24.9 | 34.1 | 37.35 | 24.9 | 9.2 | 3.25 | 9337.5 | 6225 | 2300 | 0.36948 | JRH
2016-09-19 | ds | 50 | 0.25 | 7.36 | 0 | 26.5 | 35.2 | 37.75 | 26.5 | 8.7 | 2.55 | 9437.5 | 6625 | 2175 | 0.3283 | JRH

## VFA distillation
date tested | date collected | sample | setup | sample volume mL | NaOH N | distillate initial pH | Vi mL | Vf mL NaOH pH 6 | Vf mL NaOH pH 8.3 | mL NaOH volume to pH 8.3 | recovery factor f | VFA mg per L | acetic acid standard solution mg per L | recovered over standard | using phenolphthalein as well as probe to find endpoint. First persistant pale peachy pink
| 2014-11-25 | pp | 1 | 50 | 0.1 | 3.05 | 0.2 |  | 18.9 | 18.7 | 0.8 | 2805
| 2014-11-28 | h | 1 | 50 | 0.1 | 2.98 | 0 | 36.4 | 37.4 | 37.4 | 0.8 | 5610
| 2014-11-28 | d | 1 | 50 | 0.1 | 3.71 | 2.1 |  | 3.7 | 1.6 | 0.8 | 240
| 2014-12-01 | acetic acid | 1 | 200 | 0.1 |  | 0 |  | 54.6 | 54.6 | 1 | 1638 | 2040 | 0.80294
| 2014-12-09 | pp | 1 | 50 | 0.1 | 2.51 | 0 | 18.8 | 18.8 | 18.8 | 0.8 | 2820
| 2014-12-09 | h | 2 | 50 | 0.1 | 2.21 | 0 | 41.3 | 42.5 | 42.5 | 0.8 | 6375
| 2014-12-09 | db | 3 | 50 | 0.1 | 2.95 | 8.2 | 9.3 | 9.4 | 1.2 | 0.8 | 180
| 2014-12-09 | ds | 1 | 50 | 0.1 | 2.95 | 0 | 1.5 | 1.6 | 1.6 | 0.8 | 240
| 2014-12-09 | e1 | 2 | 50 | 0.1 | 2.99 | 1.7 |  | 3.2 | 1.5 | 0.8 | 225
| 2014-12-09 | e2 | 3 | 50 | 0.1 | 3.01 | 3.3 |  | 4.7 | 1.4 | 0.8 | 210
| 2014-12-17 | liquid manure Osha | 1 | 50 | 0.1 |  | 0 |  | 21.2 | 21.2 | 0.69 | 3686.9565
| 2014-12-17 | liquid manure VTC reception | 2 | 50 | 0.1 |  | 0 |  | 16.1 | 16.1 | 0.67 | 2883.5821
| 2014-12-17 | pp | 3 | 50 | 0.1 |  | 0 |  | 31.5 | 31.5 | 0.7 | 5400
| 2014-12-17 | h | 1 | 50 | 0.1 |  | 0 |  | 66.5 | 66.5 | 0.69 | 11565.2174
| 2014-12-17 | db | 2 | 50 | 0.1 |  | 16.8 |  | 18.4 | 1.6 | 0.67 | 286.5672
| 2014-12-17 | ds | 3 | 50 | 0.1 |  | 18.4 |  | 20.8 | 2.4 | 0.7 | 411.4286
| 2014-12-17 | e2 | 1 | 50 | 0.1 |  | 0 |  | 1.3 | 1.3 | 0.69 | 226.087
| 2014-12-17 | h | 2 | 50 | 0.1 |  | 0 |  | 66.1 | 66.1 | 0.67 | 11838.806
| 2014-12-17 | db | 3 | 50 | 0.1 |  | 0 |  | 86.5 | 86.5 | 0.7 | 14828.5714
| 2014-12-18 | acetic acid | 1 | 200 | 0.1 |  | 0 |  | 47.1 | 47.1 | 1 | 1413 | 2040 | 0.69265
| 2014-12-18 | acetic acid | 2 | 200 | 0.1 |  | 0 |  | 45.5 | 45.5 | 1 | 1365 | 2040 | 0.66912
| 2014-12-18 | acetic acid | 3 | 200 | 0.1 |  | 0 |  | 47.9 | 47.9 | 1 | 1437 | 2040 | 0.70441
| 2015-01-07 | acetic acid | 1 | 200 | 0.1 | 3.19 | 0 | 45 | 47.5 | 47.5 | 1 | 1425 | 2040 | 0.69853 | clean condenser
| 2015-01-07 | acetic acid | 2 | 200 | 0.1 | 3.35 | 0 | 41.9 | 44.9 | 44.9 | 1 | 1347 | 2040 | 0.66029 | clean condenser
| 2015-01-07 | acetic acid | 3 | 200 | 0.1 | 3.31 | 0 | 38.7 | 41.7 | 41.7 | 1 | 1251 | 2040 | 0.61324 | clean condenser
| 2015-01-20 | acetic acid | 1 | 200 | 0.1 | 3.57 | 0 | 43.4 | 47.7 | 47.7 | 1 | 1431 | 2040 | 0.70147 | setup moved to chemestry lab
| 2015-01-20 | h | 2 | 50 | 0.1 | 3.44 | 0 | 54.7 | 60.3 | 60.3 | 70 | 103.3714
| 2015-01-20 | ds | 3 | 50 | 0.1 | 3.92 | 10.4 | 12.2 | 12.5 | 2.1 | 70 | 3.6
| 2015-08-11 | acetic acid | 1 | 200 | 0.1 | 2.9 | 0 | 47.5 | 49.5 | 49.5 | 1 | 1485 | 2040 | 0.72794 | let distill too long, poured out 12 mL to reach 150
|  |  | 2 | 200 | 0.1 | 3.14 | 0 | [6 empty] | 0.67 | numbers missing from spreadsheet. Had recovery rate in email.
|  |  | 3 | 200 | 0.1 | [8 empty] | 0.67 | numbers missing from spreadsheet. Had recovery rate in email.
Note on P29: Nuite, Zyla: setup moved to chemestry lab. trouble getting hotplates to same temp technician having bad day.

## curves
2015-07-28
2015-07-07 |  | 2015-07-14 |  |  | 17 mL NaOH 0.1M mixed 1/20/15 |  | 20 mL NaOH
V H2SO4 | pH | V H2SO4 | pH |  | V H2SO4 .25N 7/24/25 | pH | V KHP .05N | pH
0 | 7.2 | 0 | 7.34 |  | 0 | 11.78 | 0 | 11.76
0.5 | 7.08 | 0.5 | 7.2 |  | 0.5 | 11.79 | 0.5 | 11.76
1 | 7 | 1 | 7.03 |  | 1 | 11.8 | 1 | 11.76
1.5 | 6.9 | 1.5 | 6.94 |  | 1.5 | 11.8 | 1.5 | 11.77
2 | 6.82 | 2 | 6.86 |  | 2 | 11.79 | 2 | 11.78
2.5 | 6.73 | 2.5 | 6.76 |  | 2.5 | 11.78 | 2.5 | 11.78
3 | 6.68 | 3 | 6.71 |  | 3 | 11.77 | 3 | 11.79
3.5 | 6.61 | 3.5 | 6.64 |  | 3.5 | 11.75 | 3.5 | 11.79
4 | 6.56 | 4 | 6.59 |  | 4 | 11.72 | 4 | 11.8
4.5 | 6.52 | 4.5 | 6.55 |  | 4.5 | 11.69 | 4.5 | 11.8
5 | 6.46 | 5 | 6.5 |  | 5 | 11.65 | 5 | 11.82
5.5 | 6.41 | 5.5 | 6.46 |  | 5.5 | 11.59 | 5.5 | 11.82
6 | 6.37 | 6 | 6.41 |  | 6 | 11.51 | 6 | 11.82
6.5 | 6.32 | 6.5 | 6.38 |  | 6.5 | 11.37 | 6.5 | 11.83
7 | 6.27 | 7 | 6.34 |  | 7 | 11.06 | 7 | 11.83
7.5 | 6.23 | 7.5 | 6.28 |  | 7.5 | 9.63 | 7.5 | 11.83
8 | 6.2 | 8 | 6.23 |  | 8 | 3.65 | 8 | 11.83
8.5 | 6.15 | 8.5 | 6.19 |  | 8.5 | 2.68 | 8.5 | 11.83
9 | 6.12 | 9 | 6.14 |  | 9 | 2.46 | 9 | 11.83
9.5 | 6.06 | 9.5 | 6.08 |  | 9.5 | 2.31 | 9.5 | 11.83
10 | 6.01 | 10 | 6.03 |  | 10 | 2.21 | 10 | 11.82
10.5 | 5.96 | 10.5 | 5.97 |  | 10.5 | 2.13 | 10.5 | 11.82
11 | 5.9 | 11 | 5.91 |  | 11 | 2.08 | 11 | 11.82
11.5 | 5.83 | 11.5 | 5.84 |  | 11.5 | 2.03 | 11.5 | 11.82
12 | 5.76 | 12 | 5.79 |  | 12 | 2 | 12 | 11.81
12.5 | 5.68 | 12.5 | 5.71 |  |  |  | 12.5 | 11.8
13 | 5.6 | 13 | 5.63 |  |  |  | 13 | 11.8
13.5 | 5.49 | 13.5 | 5.55 |  |  |  | 13.5 | 11.8
14 | 5.39 | 14 | 5.44 |  |  |  | 14 | 11.79
14.5 | 5.28 | 14.5 | 5.34 |  |  |  | 14.5 | 11.79
15 | 5.17 | 15 | 5.23 |  |  |  | 15 | 11.78
15.5 | 5.03 | 15.5 | 5.11 |  |  |  | 15.5 | 11.78
16 | 4.89 | 16 | 4.98 |  |  |  | 16 | 11.77
16.5 | 4.77 | 16.5 | 4.83 |  |  |  | 16.5 | 11.76
17 | 4.62 | 17 | 4.71 |  |  |  | 17 | 11.76
17.5 | 4.53 | 17.5 | 4.57 |  |  |  | 17.5 | 11.75
18 | 4.45 | 18 | 4.49 |  |  |  | 18 | 11.74
18.5 | 4.39 | 18.5 | 4.4 |  |  |  | 18.5 | 11.73
19 | 4.31 | 19 | 4.33 |  |  |  | 19 | 11.72
19.5 | 4.23 | 19.5 | 4.24 |  |  |  | 19.5 | 11.71
20 | 4.14 | 20 | 4.14 |  |  |  | 20 | 11.7
20.5 | 4.08 | 20.5 | 4.05 |  |  |  | 20.5 | 11.68
21 | 4 | 21 | 3.96 |  |  |  | 21 | 11.68
21.5 | 3.92 | 21.5 | 3.88 | 4.13 |  |  | 21.5 | 11.66
22 | 3.8 | [5 empty] | 22 | 11.65
22.5 | 3.73 | [5 empty] | 22.5 | 11.64
23 | 3.55 | [5 empty] | 23 | 11.62
23.5 | 3.38 | [5 empty] | 23.5 | 11.61
24 | 3.21 | [5 empty] | 24 | 11.6
24.5 | 3.06 | [5 empty] | 24.5 | 11.58
25 | 2.93 | [5 empty] | 25 | 11.56
25.5 | 2.83 | [5 empty] | 25.5 | 11.54
26 | 2.72 | [5 empty] | 26 | 11.53
26.5 | 2.65 | [5 empty] | 26.5 | 11.51
27 | 2.57 | [5 empty] | 27 | 11.49
27.5 | 2.51 | [5 empty] | 27.5 | 11.46
28 | 2.45 | [5 empty] | 28 | 11.44
28.5 | 2.39 | [5 empty] | 28.5 | 11.42
29 | 2.35 | [5 empty] | 29 | 11.38
29.5 | 2.31 | [5 empty] | 29.5 | 11.36
30 | 2.27 | [5 empty] | 30 | 11.32
30.5 | 2.23 | [5 empty] | 30.5 | 11.29
31 | 2.2 | [5 empty] | 31 | 11.24
31.5 | 2.16 | [5 empty] | 31.5 | 11.2
32 | 2.14 | [5 empty] | 32 | 11.15
32.5 | 2.11 | [5 empty] | 32.5 | 11.09
33 | 2.08 | [5 empty] | 33 | 11.03
33.5 | 2.06 | [5 empty] | 33.5 | 10.94
34 | 2.04 | [5 empty] | 34 | 10.85
34.5 | 2.02 | [5 empty] | 34.5 | 10.73
35 | 2 | [5 empty] | 35 | 10.59
35.5 | 1.98 | [5 empty] | 35.5 | 10.4
36 | 1.96 | [5 empty] | 36 | 10.23
36.5 | 1.94 | [5 empty] | 36.5 | 9.99
37 | 1.93 | [5 empty] | 37 | 9.78
37.5 | 1.91 | [5 empty] | 37.5 | 9.54
38 | 1.9 | [5 empty] | 38 | 9.25
38.5 | 1.88 | [5 empty] | 38.5 | 8.79
39 | 1.87 | [5 empty] | 39 | 7.74
39.5 | 1.86 | [5 empty] | 39.5 | 7
40 | 1.85 | [5 empty] | 40 | 6.72
[7 empty] | 40.5 | 6.56
[7 empty] | 41 | 6.45
[7 empty] | 41.5 | 6.34
[7 empty] | 42 | 6.28
[7 empty] | 42.5 | 6.2
[7 empty] | 43 | 6.13
[7 empty] | 43.5 | 6.09
[7 empty] | 44 | 6.03
[7 empty] | 44.5 | 5.99
[7 empty] | 45 | 5.95
[7 empty] | 45.5 | 5.91
[7 empty] | 46 | 5.88
[7 empty] | 46.5 | 5.84
[7 empty] | 47 | 5.81
[7 empty] | 47.5 | 5.77
[7 empty] | 48 | 5.75
[7 empty] | 48.5 | 5.72
[7 empty] | 49 | 5.7
[7 empty] | 49.5 | 5.68
[7 empty] | 50 | 5.66

## Sheet1
date collected | sample location | sample volume mL | H2SO4 N | pH initial | H2SO4 Vi ml | H2SO4 Vf at pH 5.75 | H2SO4 Vf at pH 4.3 | H2SO4 Vf at pH 4.0 | notes | initials
|  | 50 | 0.25

## t curves
date | sample | H2SO4 N | 0 | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 17.5 | 18 | 18.5 | 19 | 19.5 | 20 | 20.5 | 21 | 21.5 | 22 | 22.5 | 23 | 23.5 | 24 | 24.5 | 25 | 25.5 | 26 | 26.5 | 27 | 27.5 | 28 | 28.5 | 29 | 29.5 | 30 | 30.5 | 31 | 31.5 | 32 | 32.5 | 33 | 33.5 | 34 | 34.5 | 35 | 35.5 | 36 | 36.5 | 37 | 37.5 | 38 | 38.5 | 39 | 39.5 | 40
2015-07-21 | ds | 0.25 | 7.39 | 7.24 | 7.13 | 7.01 | 6.92 | 6.83 | 6.77 | 6.71 | 6.67 | 6.62 | 6.57 | 6.52 | 6.48 | 6.44 | 6.4 | 6.37 | 6.34 | 6.3 | 6.27 | 6.24 | 6.2 | 6.15 | 6.12 | 6.08 | 6.04 | 5.98 | 5.93 | 5.87 | 5.82 | 5.73 | 5.65 | 5.55 | 5.44 | 5.33 | 5.17 | 5 | 4.77 | 4.68 | 4.62 | 4.52 | 4.37 | 4.31 | 4.12 | 3.97 | 3.67 | 3.41 | 3.17 | 2.99 | 2.86