## Sheet1
VTCAD May 2015 Operational Data
notes: AD vertical mixing pump 6 out all month. | Day of May 2015 | biogas consumed (m3) | CH4 (%) | H2S (ppm) | day | electricity consumed (kWh) | electricity produced (kWh) | Hydrolyzer pH | AD pH | day | hydroylzer Ripley ratio | AD Ripley ratio | day | Hydrolyzer TA (mg/L CaCO3) | hydrolyzer PA (mg/L CaCO3) | hydrolyzer IA (mg/L CaCO3) | AD TA (mg/L CaCO3) | AD PA (mg/L CaCO3) | AD IA (mg/L CaCO3) | generator starts | flare starts | 2G cumulative biogas (m3) | generator cumulative operation (hrs)
AD vertical mixing pump out all month. Worked on flare: raised position of thermocouple. | 1 | 1691.5717 | 60.3 | 222 | 1 | 694.3018 | 4035.9674 | 5.02 | 7.22 | 1 |  | 0.41667 | 1 | 1918.3333 |  | 1073.6667 | 6266.6667 | 4220 | 1742.6667
Conveyer 2 breaker tripped. | 2 | 1939.0202 |  | 174 | 2 | 641.1527 | 4885.4179 | 5.06 | 7.22 | 2 |  |  | 2
Conveyer 2 breaker tripped. | 3 | 1746.7826 |  | 266 | 3 | 590.6087 | 5017.0435 | 5.04 | 7.22 | 3 |  |  | 3
| 4 |  |  |  | 4 |  |  |  |  | 4 |  |  | 4
| 5 |  |  |  | 5 |  |  |  |  | 5 |  |  | 5
| 6 | 1624.761 | 62.3 | 194 | 6 | 646.4965 | 5000.9095 | 5.1 | 7.23 | 6 |  |  | 6
| 7 | 1614.0881 | 61.2 | 364 | 7 | 672.2013 | 5689.5597 | 5.03 | 7.18 | 7 |  |  | 7
Increased glycerol:crumb to 800 gallons/day. Increased flare on setting to 90%. Genset on setting is 80%. Calibrated gas analyzer. | 8 | 1594.912 | 61.4 | 289 | 8 | 623.5453 | 5422.8958 | 5.02 | 7.24 | 8 |  | 0.48 | 8 | 2450 |  | 1633.3333 | 6083.3333 | 3875 | 1866.6667
| 9 |  |  |  | 9 |  |  |  |  | 9 |  |  | 9
Changed FeCl3 tote. | 10 | 1641.9299 | 60.7 | 369 | 10 | 581.2982 | 5229.6841 |  |  | 10 |  |  | 10
| 11 | 2137.0637 | 60.5 | 350 | 11 | 561.4404 | 4945.2632 |  |  | 11 |  |  | 11
Genset tripped off x 2; flare worked first time but was turned off second time? | 12 | 1882.5974 | 60.3 | 275 | 12 | 554.8052 | 4431.1688 | 5.25 | 7.17 | 12 |  |  | 12
| 13 | 1351.6138 | 60 | 262 | 13 | 628.6345 | 3031.9448 | 5.25 | 7.23 | 13 |  |  | 13
| 14 | 1708.4082 | 60.5 | 342 | 14 | 491.7551 | 4415.0204 |  |  | 14 |  |  | 14
| 15 | 1783.7288 | 60.3 | 330 | 15 | 627.4576 | 4448.1356 | 5.14 | 7.32 | 15 |  | 0.6075 | 15 | 2825 |  | 2025 | 6168.75 | 3637.5 | 2200
Ammonia in prep pit; connected to moldy silage fed yesterday? | 16 | 1964.1926 | 60 | 323 | 16 | 509.915 | 4303.6827 | 5.19 | 7.15 | 16 |  |  | 16
| 17 |  | 59.9 | 358 | 17 |  |  |  |  | 17 |  |  | 17
Flushed ~100 gallons from bottom of AD tank. | 18 | 4249.61 | 59.6 | 432 | 18 | 1207.8627 | 9188.8924 | 5.35 | 7.13 | 18 |  |  | 18
| 19 | 1870.9202 | 59.5 | 295 | 19 | 596.8098 | 4032.3926 | 5.13 | 7.13 | 19 |  |  | 19
| 20 |  |  |  | 20 |  |  |  |  | 20 |  |  | 20
Flushed ~1000 gallons from bottom of AD tank. | 21 | 1945.1309 | 60.2 | 320 | 21 | 549.3613 | 4200.8796 | 5.04 | 7.21 | 21 |  | 0.63667 | 21 | 2491.6667 |  | 1725 | 6066.3333 | 3458.3333 | 2200
Pump 11 running fault | 22 | 2052.3789 | 61.1 | 480 | 22 | 496.1684 | 4417.0105 |  |  | 22 |  |  | 22
Pump 12 running fault | 23 | 1579 | 62.3 | 329 | 23 | 532 | 4566 | 5.19 | 7.13 | 23 |  |  | 23
Genset tripped off; flare working. Conveyer 2 breaker tripped. | 24 | 1348.3183 | 63.2 | 413 | 24 | 577.9931 | 5140.1522 |  |  | 24 |  |  | 24
| 25 | 1535.3379 | 63.2 | 333 | 25 | 504.4966 | 6031.1172 | 5.11 | 7.13 | 25 |  |  | 25
| 26 | 1536 | 62 | 367 | 26 | 530 | 5710 | 5.43 | 7.05 | 26 |  |  | 26
Lightning storm shut system down; Dan reset. Calibrated gas analyzer. | 27 | 2178.436 | 61.8 | 400 | 27 | 589.9516 | 5443.1003 | 5.19 | 7.03 | 27 |  |  | 27
Ammonia in prep pit | 28 | 1749.0732 | 60.7 | 263 | 28 | 437.5192 | 4815.7213 | 5.13 | 6.99 | 28 |  |  | 28
Genset switch closing fault | 29 | 1784.2827 | 61.9 | 196 | 29 | 540.8732 | 5414.7193 | 5.35 | 7.12 | 29 |  | 0.83667 | 29 | 2683.3333 |  | 1958.3333 | 5650 | 2850 | 2391.6667
Genset tripped off; flare working | 30 | 588.4955 |  |  | 30 | 544.1568 | 1960.9797 |  |  | 30 |  |  | 30
| 31 | 1756.4265 |  |  | 31 | 531.1816 | 5313.8905 |  |  | 31 |  |  | 31
| average | 1802.08 | 60.9957 | 317.84 | average | 594.6918 | 4888.1365 | 5.1589 | 7.1632 |  |  | 0.5955 | average | 2473.6667 |  | 1683.0667 | 6047.0167 | 3608.1667 | 2080.2
| SD | 587.2612 | 1.0856 | 75.8621 | SD | 138.9949 | 1226.8537 | 0.12183 | 0.081176 |  |  | 0.16227 | SD | 345.2081 |  | 376.9252 | 235.7856 | 510.8002 | 267.0397